## Sheet1
Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works.. etc ( upto 200 Characters) | Item Short Description ( upto 100 Characters) | APSS / Morth Cl. Number ( upto 200 Characters) | Rate (INR) ( Upto 2 Decimals ) | UOM ( upto 50 Characters) | Amount (INR) ( Upto 2 Decimals )
46 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1/8.0 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 27600
38 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 91200
3.268 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes (0.086 Cu.Mt)*38 = 3.268 M3 with 40mm HBG metal. | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 21500.172
33.44 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*38 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 220001.76
1.178 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.)*38 | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 4585.954
38 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 18430
7.7 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 50820
193.3 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 63340.544
9 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 40500
11 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 35200
1 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 3200
2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
20 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 2840
37.026 | Excavation of pit in all types of soils of size (2.2x2.2x0.85Mts)*9.for Construction of Plinths for VCB (33KV & 11 KV ) | Electrical work | Excavation of Pit for VCB | As per relevent standard specification | 331 | M3 | 12255.606
42.534 | Providing of Base concreting (2.2x2.2x0.15 Mts)*9 with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts)*9 with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Earth work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 279831.186
3 | Erection of 33kv VCB: Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. Note: Switch gear panel should be equiped with IED relay scheme, auto reset master trip relay, Announciation relay, healthy trip circuit supervision relay. Along with other metering and measuring schemes with local and remote operating facility | Electrical work | Erection of 33kv VCB | As per relevent standard specification | 12500 | M3 | 37500
6 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. Note: Switch gear panel should be equiped with IED relay scheme, auto reset master trip relay, Announciation relay, healthy trip circuit supervision relay. Along with other metering and measuring schemes with local and remote operating facility | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 72000
2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
4 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 2020
32 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 111552
32 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 39494.4
620 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 40300
1240 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 50840
4 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 18900
1 | Erection of 220 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-220V Batery with Chrgr incl grot-SS | As per relevent standard specification | 6442.58 | EA | 6442.58
1300 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | RMT | 35100
1 | Erection of 25 kVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT Distribution box w/o box | As per relevent standard specification | 1594.67 | EA | 1594.67
1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
4 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing ofPT marshall box | As per relevent standard specification | 1139.85 | EA | 4559.4
1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
4 | Supply of Earth Discharging Rod 8 feet length, 3 mm thickness. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
230 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 27025
72 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 9360
350 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 17500
38 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 15477.02
8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
9 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 24483.06
13.9 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 8577.69
13.9 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 3071.9
13.9 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 2571.5
580 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1740
580 | Unloading and unwinding of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 1160
3 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 6
3 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 6
3 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 195
3 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 195
3 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 3
3 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 3
1300 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 1300
1300 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 1326
1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
2 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 330
6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
12 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 384
12 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 384
3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
9 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 1134
9 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 711
9 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
9 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
1 | Loading of 220V Battery with charger . | Electrical work | Loading of 220V Battery with charger . | As per relevent standard specification | 1612 | EA | 1612
1 | un Loading of 220V Battery with charger . | Electrical work | un Loading of 220V Battery with charger . | As per relevent standard specification | 1024 | EA | 1024
1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
2 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 256
1 | Erection of 33 KV single phase PTs | Electrical work | Erection of 33 kv single phase PTs | As per relevent standard specification | 1079 | EA | 1079
1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse set | As per relevent standard specification | 1733.75 | EA | 1733.75
1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erection of 11KV HG Fuse set | As per relevent standard specification | 740.52 | EA | 740.52
2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
1.01 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 772.65
8 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 14076
1.01 | Paving of the 100 sqmm 6 AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 6 Cond DC | As per relevent standard specification | 24606 | KM | 24852.06
200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
3 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 606
3 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 300
3 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 8161.02
0.11 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 67.881
0.11 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 24.31
0.11 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 20.35
9 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 27
9 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 27
5 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 10
5 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 10
2 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
2 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
16 | Supply of Galvanised M+3 Tower as per ASCI Standard. Supply of Galvanised M+3 type tower as per Specification. i.e. 1.34 MT per each tower including the following terms. Supply of Suitable Hot dip Galvanised, Zinc coated Nuts and bolts with suitable plain and spring washers of 158 Kgs per each M+3 tower. Supply of material for Painting of structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 litres of thinner 1st coat is to be applied before erection of tower and 2nd coat after stringing. Supply of material for 2 nos. Pipe earthing of towers with 40mm dia GI pipe, including cost of pipe, bentonite powder and running of GI flat etc., per each tower. | Electrical work | S-M+3 Tower GALV | As per relevent standard specification | 140674.3 | EA | 2250788.8
16 | Supply of extension of 3mtrs for M+3 Tower as per ASCI Standard. Supply of Galvanised M+3 type tower as per Specification @ 0.33 MT per each M+3 tower. Supply of Suitable Hot dip Galvanised, Zinc coated Nuts and bolts with suitable plain and spring washers @ 30.23 Kgs per each tower. Supply of material for Painting of structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 litres of thinner 1st coat is to be applied before erection of tower and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Electrical work | S-Mat. for Extn of M+3 Tower by 3M GALV | As per relevent standard specification | 28520.64 | EA | 456330.24
16 | Erection of M+3 Tower, as per the following terms: Fabrication of tower Parts as per Specification @ 1.34 MT per each M+3 Tower . Setting of stubs in position for laying of foundation of towers with 1:2:4 cc mix using 40 mm HBG metal including cost of all concreting materials, form boxes and cement and curing for 14 days (40 mm HBG metal for pyramid portion and 20 mm HBG metal for concreting per each tower . Erection of tower parts completely as per specifications including erection of insulators with all accessories, jumpering,transport of meterial and bolts and nuts etc., Tack welding of total tower nuts and bolts . Including labour for Pipe earthing of towers with 40mm dia GI pipe, including cost of pipe, bentonite powder and running of GI flat etc., Transport of Material to site including loading and unloading. Labour charges for painting including scratching and cleaning of tower parts. | Electrical work | Erect-M+3 Tower (as per DATA-VII) | As per relevent standard specification | 71890.2 | EA | 1150243.2
16 | Erection of 3M extension for tower parts completely as per specifications including erection of insulators with all accessories, jumpering,transport of meterial and bolts and nuts etc., Transport of Material to site including loading and unloading. Labour charges for painting including scratching and cleaning of tower . | Electrical work | Erect-Extn of 3M for M+3 Tower | As per relevent standard specification | 5725.77 | EA | 91612.32
5 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 3422.65
16 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 8320
4.6 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 3519
8 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mtrs PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 5600
6 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 14400
3.2 | Stringing of HT AB Cable 11 KV 3x185+70 Sqmm with GI Metal Parts | Electrical work | Stringing of AB cbl 11 KV 3x185+70 Sqmm | As per relevent standard specification | 41876.1 | KM | 134003.52
3 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 9600
3 | Supply of CI eath pipe with 50mm dia,2.0 M Length with material |  | S-CI Pipe earthing 50mm dia 2m long | As per relevent standard specification | 2441 | EA | 7323
3 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 3702.6
71 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock w/o blasting. | Electrical work | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 840 | EA | 59640
18.5 | Formation of horizontal Cut point for 11 KV Single Circuit line excluding pole erection and stays | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 24975
14 | Supply and ere Straight line Asmbly kits for Stringing of HT AB Cable with GI Metal Parts | Electrical work | Supply and ere Straight line Asmbly kits | As per relevent standard specification | 1661 | EA | 23254
14 | Supply and ere Angle line Asmbly kits for Stringing of HT AB Cable with GI Metal Parts | Electrical work | Supply and ere Angle line Asmbly kits | As per relevent standard specification | 2124 | EA | 29736
14 | End Termination of AB cable 120 Sqmm to 185 Sqmm | Electrical work | End Termnatn of AB cable 120 | As per relevent standard specification | 800 | EA | 11200
100 | Supply of Suspension Clamp Assembly & Eye HookMSubmission of auto CAD Drawing as per pole schedule (Detailed survey and sketch | Electrical work | S-Suspension Clamp Assembly & Eye Hook-M | As per relevent standard specification | 65 | EA | 6500
18 | Supply of Dead End Clamp Assembly & Eye HookMSubmission of auto CAD Drawing as per pole schedule (Detailed survey and sketch | Electrical work | S-Dead End Clamp Assembly & Eye Hook-M | As per relevent standard specification | 80 | EA | 1440
101 | Supply- I Hook for Stringing of HT AB Cable with GI Metal Parts | Electrical work | Supply- I Hook | As per relevent standard specification | 158 | EA | 15958
101 | Erection of - I Hook for Stringing of HT AB Cable with GI Metal Parts | Electrical work | Erection- I Hook | As per relevent standard specification | 55 | EA | 5555
100 | Erection of Suspension Clamp Assbl & Eye Hook | Electrical work | Erect-Suspension Clamp Assbl &Eye Hook | As per relevent standard specification | 8 | EA | 800
18 | Erection of Dead End Clamp Assbl & Eye Hook | Electrical work | Erect-Dead End Clamp Assbl & Eye Hook | As per relevent standard specification | 8 | EA | 144
14 | Erection of Assemble Kit for 'T' Branche for Stringing of HT AB Cable with GI Metal Parts | Electrical work | Erection of Assemble Kit for 'T' Branche | As per relevent standard specification | 1800 | EA | 25200
77 | Transport of 9.1 M long PSCC poles (Including loading and unloading) upto Workspot upto 10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 31361.33
200 | Supply of MS bolts & nuts and washers etc of all sizes | Electrical work | S-MS Bolts & Nuts,Washers etc., | As per relevent standard specification | 91.25 | KG | 18250
28.42 | Concreting the location after erection of 12.5Mtrs/11 Mtrs pole/9.1 Mtrs poles with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. ,2 No's11.0 mtr poles (0.76x0.76x1.83mtrs)*2 = 2.11 cu mtr and 30 No's 9.1 mtr poles (0.76x0.76x1.52mtrs)*30 = 26.31 cu mtr. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 186975.18
8 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 33322.24
77 | Excavation of Pole pits of size 0.76x0.76x1.52 Mts' for 9.1 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, except Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT 0.76 M x 0.76 M x 1.52 M | As per relevent standard specification | 619.65 | EA | 47713.05
8 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 3455.76
3 | Excavation of Pole pits of size 0.76x0.76x1.52 Mts' for 8 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 5040
3 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Earth work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 1158
0.99 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 8415
0.41 | Paving of the conductor 55 Sqmm Double Circuit (6 Conductors) and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Electrical work | Stringing of 55sqmm 33/11kv Line 6 Cond | As per relevent standard specification | 16000 | KM | 6560
0.724 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 160.004
0.724 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 133.94
113 | Loading 11KV Polymer Pin Insulator with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 113
113 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 113
0.724 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 425.3645
9 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 33222.42
9 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 1818
9 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 900
5 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 20
5 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V -Cross arms | As per relevent standard specification | 4 | EA | 20
14 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 672
14 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 672
14 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 28
14 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 28
9 | Supply of Galvanised M+3 Tower as per ASCI Standard. Supply of Galvanised M+3 type tower as per Specification. i.e. 1.34 MT per each tower including the following terms. Supply of Suitable Hot dip Galvanised, Zinc coated Nuts and bolts with suitable plain and spring washers of 158 Kgs per each M+3 tower. Supply of material for Painting of structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 litres of thinner 1st coat is to be applied before erection of tower and 2nd coat after stringing. Supply of material for 2 nos. Pipe earthing of towers with 40mm dia GI pipe, including cost of pipe, bentonite powder and running of GI flat etc., per each tower. | Electrical work | S-M+3 Tower GALV | As per relevent standard specification | 140674.3 | EA | 1266068.7
9 | Supply of extension of 3mtrs for M+3 Tower as per ASCI Standard. Supply of Galvanised M+3 type tower as per Specification @ 0.33 MT per each M+3 tower. Supply of Suitable Hot dip Galvanised, Zinc coated Nuts and bolts with suitable plain and spring washers @ 30.23 Kgs per each tower. Supply of material for Painting of structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 litres of thinner 1st coat is to be applied before erection of tower and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Electrical work | S-Mat. for Extn of M+3 Tower by 3M GALV | As per relevent standard specification | 28520.64 | EA | 256685.76
9 | Erection of M+3 Tower, as per the following terms: Fabrication of tower Parts as per Specification @ 1.34 MT per each M+3 Tower . Setting of stubs in position for laying of foundation of towers with 1:2:4 cc mix using 40 mm HBG metal including cost of all concreting materials, form boxes and cement and curing for 14 days (40 mm HBG metal for pyramid portion and 20 mm HBG metal for concreting per each tower . Erection of tower parts completely as per specifications including erection of insulators with all accessories, jumpering,transport of meterial and bolts and nuts etc., Tack welding of total tower nuts and bolts . Including labour for Pipe earthing of towers with 40mm dia GI pipe, including cost of pipe, bentonite powder and running of GI flat etc., Transport of Material to site including loading and unloading. Labour charges for painting including scratching and cleaning of tower parts. | Electrical work | Erect-M+3 Tower (as per DATA-VII) | As per relevent standard specification | 71890.2 | EA | 647011.8
9 | Erection of 3M extension for tower parts completely as per specifications including erection of insulators with all accessories, jumpering,transport of meterial and bolts and nuts etc., Transport of Material to site including loading and unloading. Labour charges for painting including scratching and cleaning of tower . | Electrical work | Erect-Extn of 3M for M+3 Tower | As per relevent standard specification | 5725.77 | EA | 51531.93
9 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 4680
14 | supply of ab cable 11 KV 3x185+70 Sqmm end kits | Electrical work | S-of 11KV AB cable end kits | As per relevent standard specification | 950 | EA | 13300
10 | Supply of 11KV Middle Phase Raiser | Electrical work | S-11KV Middle Phase Raiser | As per relevent standard specification | 519 | EA | 5190
2 | Erection of 33kv ABSwitch incl earthing | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
4 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra ea | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 2800
4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit exc | Electrical work | Erection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 16661.12
8 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit ex | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 19200
11.24 | Concreting the location after erection of 12.5Mtrs/11 Mtrs pole/9.1 Mtrs poles with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. ,4 No's11.0 mtr poles (0.76x0.76x1.83mtrs)*4 = 4.22 cu mtr and 8 No's 9.1 mtr poles (0.76x0.76x1.52mtrs)*8 = 7.02 cu mtr. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 73947.96
10 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 1175
0.68 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 150.28
0.68 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 125.8
0.68 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 399.5136
4 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | ea | 1727.88
8 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 3258.32
2 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 96
2 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 96
2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 4
2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 4
4 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 13944
4 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Ben | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
60 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 6300
2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
12 | Hiring of JCB for leveling of ground including cost & conveyance of all etc complete for finished item of work | Machinery | Hiring of JCB | As per relevant standard specification | 2164.1 | H | 25969.2
164.41 | Earth Work Mass Excavation (Ordinary Soil) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth work | Earth Work Mass Excavation (Ordinary Soil) | As per relevant standard specification | 347 | M3 | 57050.27
26.89 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | Concrete | PCC (1:4:8) for levelling course using 40mm | As per relevant standard specification | 4096 | M3 | 110141.44
217.52 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering, scaffolding, cutting for all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | Masonry | CRS masonry in CM (1:6) using Hard Granite Stones | As per relevant standard specification | 4464 | M3 | 971009.28
72.9 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Masonry | Construction of brick masonary in CM(1:6) | As per relevant standard specification | 7640 | M3 | 556956
882.17 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | Earth work | Supplying and filling with borrowed gravel | As per relevant standard specification | 435 | M3 | 383743.95
7.25 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (a) Footings | RCC | R.C.C M20 nominal mix (a) Footings | As per relevant standard specification | 8235 | M3 | 59703.75
6.78 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (b) Columns | RCC | R.C.C M20 nominal mix (b) Columns | As per relevant standard specification | 10931 | M3 | 74112.18
1.6 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (c) Plinth Beams | RCC | R.C.C M20 nominal mix (c) Plinth Beams | As per relevant standard specification | 10655 | M3 | 17048
0.67 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (d) Lintels | RCC | R.C.C M20 nominal mix (d) Lintels | As per relevant standard specification | 11091 | M3 | 7430.97
5.63 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (e) Sunshade | RCC | R.C.C M20 nominal mix (e) Sunshade | As per relevant standard specification | 1163 | M2 | 6547.69
2.66 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (f) Roof Beams | RCC | R.C.C M20 nominal mix (f) Roof Beams | As per relevant standard specification | 10666 | M3 | 28371.56
8.73 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (g) Slab of 130 mm thick | RCC | R.C.C M20 nominal mix (g) Slab of 130 mm thick | As per relevant standard specification | 10217 | M3 | 89194.41
2.6 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars | As per relevant standard specification | 76127 | TO | 197930.2
762.24 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | Providing plastering of 20mm thick | As per relevant standard specification | 412 | M2 | 314042.88
313.5 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Plastering | Raised pointing in CM(1:3) | As per relevant standard specification | 94 | M2 | 29469
54.87 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the rate of 1 kg per bag of cement inclding cost and conveyance of all materials | Plastering | Providing impervious coat over RCC roof slab | As per relevant standard specification | 441 | M2 | 24197.67
5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | Supply and fixing of Flush type Doors | As per relevant standard specification | 6799.02 | M2 | 38754.414
5.76 | Supply and Fixing of powder coated Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | S&F of powder coated Aluminium sliding windows with fixed glass panels | As per relevant standard specification | 3535.64 | M2 | 20365.2864
6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | MS Grills | Supplying and fixing of MS safety grill | As per relevant standard specification | 2539 | M2 | 15868.75
26.5 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | Flooring with double machine polished and hand cut Tandur blue stone | As per relevant standard specification | 660 | M2 | 17490
6.94 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | Providing skirting with tandoor blue slabs | As per relevant standard specification | 727 | M2 | 5045.38
27 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | PCC | Plain Cement contrete - Nominal Mix (1:3:6) | As per relevant standard specification | 4398 | M3 | 118746
8.19 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | PCC | PCC(1:2:4) using 10 to 12 mm aggregate | As per relevant standard specification | 5513 | M3 | 45151.47
76.92 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | HBG metal | Supply and Spreading of 20mm metal | As per relevant standard specification | 1514 | M3 | 116456.88
120 | Supply and fixing of fencing of welded wire mesh (1"x2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded mesh | Supply and fixing of fencing of welded wire mesh (1" x 2") | As per relevant standard specification | 2042 | M2 | 245040
19.17 | Supply and fixing of MS gates of approved design including cost and conveyance of all materials,fabrication charges etc complete for finished item of work. | MS gate | Supply and fixing of MS gates of approved design | As per relevant standard specification | 4579.89 | M2 | 87796.4913
235.2 | S&F Structural Steel Angles etc. | Steel angles | S&F Structural Steel Angles etc. | As per relevant standard specification | 104 | Kg | 24460.8
1120 | S&F Barbed Wire 1H | Barbed wire | S&F Barbed Wire 1H | As per relevant standard specification | 13.9 | M | 15568
104.6 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with two coats of OBD | As per relevant standard specification | 109.9 | M2 | 11495.54
377 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with two coats of ACE paint | As per relevant standard specification | 195.91 | M2 | 73858.07
210.9 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with lovely cem three coats | As per relevant standard specification | 70.47 | M2 | 14862.123
7.3 | Manufacture, supply ,laying and fixing of 450mm dia. NP3 class R.C.C. socket and spigot pipes (rate per meter of effective length) including transportaion ,taxes and duties etc. complete for finished item of work and as directed by the Engineer-in-charge. | Culvert pipe | R.C.C. socket and spigot pipes | As per relevant standard specification | 1344 | RMT | 9811.2
25 | S&F Conceal PVC Pipe 32mm dia in Slab including cost and conveyance of all material and labour charges complete for finished item of work | Electrification | S&F Conceal PVC Pipe 32mm dia in Slab | As per relevant standard specification | 85 | RMT | 2125
15 | S&F Conceal PVC Pipe 20mm dia in Wall including cost and conveyance of all material and labour charges complete for finished item of work | Electrification | S&F Conceal PVC Pipe 20mm dia in Wall | As per relevant standard specification | 89 | RMT | 1335
15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable | As per relevant standard specification | 580 | EA | 8700
2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | Supply and fixing of 6A 3/2 pin flush type plug socket | As per relevant standard specification | 469 | EA | 938
2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | Supply and fixing of 16A 3pin flush type plug socket | As per relevant standard specification | 437 | EA | 874
4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Supply and fixing of slanting holders | As per relevant standard specification | 116 | EA | 464
4 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Supply and fixing of patty type tube light fitting | As per relevant standard specification | 868 | EA | 3472
90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | Supply and run of 2 of 14/.3mm(1.00Sqmm) cu cable | As per relevant standard specification | 48 | RMT | 4320
30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | Supply and run of 2 of 36/0.3 (2.5sqmm) cu cable | As per relevant standard specification | 95 | RMT | 2850
1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | SPN Distribution board with IP-20 protection suitable for single phase 40A DP | As per relevant standard specification | 5038 | EA | 5038
1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Providing independent earthing for main switches | As per relevant standard specification | 4891 | EA | 4891
15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Electrification | Supply and run of No.8 SWG Copper wire | As per relevant standard specification | 140 | RMT | 2100
2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Supply and Fixing of 48" ceiling fan | As per relevant standard specification | 2215 | EA | 4430
15.8 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Tiles | Supply and fixing of ceramic tiles fantacy | As per relevant standard specification | 760 | M2 | 12008
1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and fixing of 580mm x 440mm long Orissa pan | As per relevant standard specification | 2178 | EA | 2178
2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and Fixing 4" PVC floor trap | As per relevant standard specification | 269 | EA | 538
2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply,fixing 90mm dia. PVC Plain Bend | As per relevant standard specification | 84 | EA | 168
1 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply,fixing 90mm dia. PVC Door Bend | As per relevant standard specification | 81 | EA | 81
1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Plumbing | S&Fixing 150mm x 100mm SWG gully trap | As per relevant standard specification | 749 | EA | 749
6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and Fixing 4" dia 3M Single socket PVC pipe | As per relevant standard specification | 422 | RMT | 2532
1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Plumbing | Supply and Fixing 4" dia PVC cowl | As per relevant standard specification | 23 | EA | 23
1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Plumbing | Construction of soak pit with 4' dia RCM rings | As per relevant standard specification | 2950 | EA | 2950
20 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 15.90mm OD Pipe - SDR 11 | Plumbing | CPVC Pipes and Fittings 15.90mm OD Pipe - SDR 11 | As per relevant standard specification | 239 | RMT | 4780
100 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 22.20mm OD Pipe - SDR 11 | Plumbing | CPVC Pipes and Fittings 22.20mm OD Pipe - SDR 11 | As per relevant standard specification | 313 | RMT | 31300
100 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 28.60mm OD Pipe - SDR 11 | Plumbing | CPVC Pipes and Fittings 28.60mm OD Pipe - SDR 11 | As per relevant standard specification | 410 | RMT | 41000
18 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and fixing of 15mm dia. SS coated taps | As per relevant standard specification | 230 | EA | 4140
1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and fixing of 20mm dia. GM Ball valve | As per relevant standard specification | 331 | EA | 331
2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and fixing of 25mm dia. GM Ball valve | As per relevant standard specification | 466 | EA | 932
3 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and fixing of 12.7mm bib tap | As per relevant standard specification | 271 | EA | 813
500 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Providing and placing on Terrace polyetheylene water storage tank | As per relevant standard specification | 10 | L | 5000
1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of steel table of size 4'x2.5'x30" | As per relevant standard specification | 4200 | EA | 4200
1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of 'S' type chair with arms teakwood | As per relevant standard specification | 3850 | EA | 3850
2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of P V C chairs | As per relevant standard specification | 1150 | EA | 2300
1.35 | Supply and Fixing of Substation name board of size 5'x3' iron sheet with angle frame and channel supports of size 75x40mm, 8' height including concreting of channel supports and painting with enamel paint complete. | Board | Supply and Fixing of Substation name board | As per relevant standard specification | 4542.3 | Sqm | 6132.105
2.21 | S&F Glow Sign Board | Board | S&F Glow Sign Board | As per relevant standard specification | 3730.36 | Sqm | 8244.0956
1 | Geophysical Investgation Charges | Bore well | Geophysical Investgation Charges | As per relevant standard specification | 5000 | EA | 5000
90 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 0 to 90M | Bore well | Drilling of 6.5" dia bore well | As per relevant standard specification | 336 | M | 30240
30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 90m to 120M | Bore well | Drilling of 6.5" dia bore well | As per relevant standard specification | 369 | M | 11070
30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 120m to 150M | Bore well | Drilling of 6.5" dia bore well | As per relevant standard specification | 394 | M | 11820
30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 150m to 180M | Bore well | Drilling of 6.5" dia bore well | As per relevant standard specification | 492 | M | 14760
30 | Suppy & fixing of 160 mm dia. 6 kg/cm2 PVC casing pipe including cost and conveyance of all materials labour charges etc complete for finished item of work | Bore well | S&F of PVC casing | As per relevant standard specification | 844 | M | 25320
1 | Supply & fixing of 2HP Multistage submersible motor pumpset of approved make (Texmo or equivalent type) including cost and conveyance of all materials etc complete for finished item of work. | Bore well | S&F of 2HP Motor pumpset | As per relevant standard specification | 34237 | EA | 34237
200 | S&R 3C 2.5sqmm Flat Copper Cable including cost of all materials and labour charges for finished item of work. | Bore well | S&F of copper cable | As per relevant standard specification | 190 | M | 38000
1 | Supply and fixing of Panel box and starter including cost of all materials and labour charges for finished item of work. | Bore well | Supply and fixing of Panel box and starter | As per relevant standard specification | 1040 | EA | 1040
2 | Supply & fixing of Flange Clamps including cost of all materials and labour charges for finished item of work. | Bore well | Supply & fixing of Flange Clamps | As per relevant standard specification | 182 | EA | 364
145 | Suppy & fixing of HDPE pipe 1.5" dia. including cost & conveyance of all materials labour charges etc complete for finished item of work. | Bore well | Suppy & fixing of HDPE pipe | As per relevant standard specification | 160 | Rmt | 23200
148.1 | Seigniorage Charges - Sand | Seigniorages | Seigniorage Charges - Sand | As per relevant standard specification | 40 | M3 | 5924
107.5 | Seigniorage Charges - Metal | Seigniorages | Seigniorage Charges - Metal | As per relevant standard specification | 97.5 | M3 | 10481.25
882.17 | Seigniorage Charges - Gravel | Seigniorages | Seigniorage Charges - Gravel | As per relevant standard specification | 30 | M3 | 26465.1
13051989.0304