## Sheet1
Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works.. etc ( upto 200 Characters) | Item Short Description ( upto 100 Characters) | APSS / Morth Cl. Number ( upto 200 Characters) | Rate (INR) ( Upto 2 Decimals ) | UOM ( upto 50 Characters) | Amount (INR) ( Upto 2 Decimals )
6 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Electrical work | Supply 9mtrs tubular poles single way | As per relevent standard specification | 13913 | EA | 83478
6 | Erection of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Electrical work | Errection of tubular poles | As per relevent standard specification | 1379 | EA | 8274
2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
1 | Erection of 3 Phase DTRs 63,75 & 100 KVA including loading and Unloading DTR on the Structure/Plinth etc | Electrical work | E/r 3ph DTR inclu L&Un-L,T&C on plinth | As per relevent standard specification | 1650 | EA | 1650
1 | Construction of DTR Plinth CRS 5x4x8', 4' thck | civil work | Construct-DTR Plinth CRS 5x4x8', 4' thck | As per relevent standard specification | 13750 | EA | 13750
1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
1700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Electrical work | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | M | 45900
1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
1 | Erectionofcontrol/Relaypanels,ACPanels,announciationpanelsetcin thecontrol roomdulymountingthemonchannelsandgroutingthemwith foundation bolts excluding cost of channels & foundation bolts | Electrical work | Erect-Contrl/Relay, AC, Announ. Panels | As per relevent standard specification | 1930 | EA | 1930
10 | Loading of 33 KV VCBs along with Panel boards | Electrical work | LOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 10240
10 | Un loading of 33 KV VCBs along with Panel boards | Electrical work | UNLOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 10444.8
10 | Transport of Above 10 Km and upto 20 Km with Lorry for each tripconductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transforme | Electrical work | Transport of Cond Drum,VCBs >10 & <20Km | As per relevent standard specification | 3299.7 | EA | 32997
10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel Note: Switch gear panel should be equiped with IED relay scheme, auto reset master trip relay, Announciation relay, healthy trip circuit supervision relay. Along with other metering and measuring schemes with local and remote operating facility | Electrical work | Erection of 33KV indoor switchgear panel | As per relevent standard specification | 9847 | EA | 98470
750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Electrical work | Supply,fabricati of 6mm Checkerd plates | As per relevent standard specification | 83 | KG | 62250
20 | Rubber mats ( 6’x3’) size for indoor SS | Electrical work | SupRubber mats( 6#x3#)size fo indoorSS | As per relevent standard specification | 1386 | EA | 27720
1 | S-10ft Aluminium Ladder | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
2 | Trolley mounted CO2 (6.5Kgs) | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
2 | Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 2772
6 | Room fire extinguisher (2 ltrs capacity) for control room | Electrical work | Sup Fire Extinguisher for Control Room | As per relevent standard specification | 4620 | EA | 27720
4 | Supply of Safety Helmet of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 924
4 | Sup Earth Rods (8ft) Screw & clamp type | Electrical work | Sup Earth Rods (8ft) Screw & clamp type | As per relevent standard specification | 578 | EA | 2312
4 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 1156
1 | Sup Stand basic cell phone with charger | Electrical work | Sup Stand basic cell phone with charger | As per relevent standard specification | 1386 | EA | 1386
1 | Sup Steel almarah(61/2 X 3ft) Godrej | Electrical work | Sup Steel almarah(61/2 X 3ft) Godrej | As per relevent standard specification | 9818 | EA | 9818
1 | Supply of Table (3x6ft) Godrej | Electrical work | Supply of Table (3x6ft) Godrej | As per relevent standard specification | 6050 | EA | 6050
4 | Supply of S type chairs (Godrej) | Electrical work | Supply of S type chairs (Godrej) | As per relevent standard specification | 924 | EA | 3696
1 | Sup Angle racks(18x36.6inches) Godrej | Electrical work | Sup Angle racks(18x36.6inches) Godrej | As per relevent standard specification | 1733 | EA | 1733
10 | Supply of Danger boards with clamps | Electrical work | Supply of Danger boards with clamps | As per relevent standard specification | 116 | EA | 1160
1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
1 | Supply of Wall clock standard make | Electrical work | Supply of Wall clock standard make | As per relevent standard specification | 578 | EA | 578
1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
1 | Sup Rechargeable LED torch light. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
1 | Supply of Hack saw (12 inches) | Electrical work | Supply of Hack saw (12 inches) | As per relevent standard specification | 289 | EA | 289
8 | Supply of LC Boards | Electrical work | Supply of LC Boards | As per relevent standard specification | 116 | EA | 928
2 | Supply of Gum Boots | Electrical work | Supply of Gum Boots | As per relevent standard specification | 693 | EA | 1386
1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
1 | Supply of 5000v megger | Electrical work | Supply of 5000v megger | As per relevent standard specification | 13860 | EA | 13860
1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
6 | Supply of 90W LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty | Electrical work | S-90W LED fixture set | As per relevent standard specification | 8200 | EA | 49200
26 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 90636
2 | Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Electrical work | S-GI pipe earthing 40mm dia 2m long | As per relevent standard specification | 698 | EA | 1396
7.92 | Concreting the location after erection of 12.5Mtrs/11 Mtrs pole/9.1 Mtrs poles with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. ,9 No's 9.1 mtr poles (0.76x0.76x1.52mtrs)*9 = 7.9 cu mtr. | Earth Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 52105.68
90 | Laying of Single Run with LT 3.5x185sqmm UG Cb HG/BC/CC/BT | Electrical work | Lay-SR LT 3.5x185sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 377.63 | M | 33986.7
10 | Raising of Single Run with LT 3.5x185sqmm UG Cb HG/BC/CC/BT | Electrical work | Raise-SR LT 3.5x185sqmm UG Cb on support | As per relevent standard specification | 85.43 | M | 854.3
2 | Supply of 31/2x185Sqmm UG O/D end term kits | Electrical work | Sup of 31/2x185Sqmm UG O/D end term kits | As per relevent standard specification | 550 | EA | 1100
2 | Making of Outdoor/Indoor End Termination OF LT 3 1/2 x 185 | Electrical work | OD/Idoor end termination LT 3 1/2 x 185 | As per relevent standard specification | 968.9 | EA | 1937.8
50 | Laying of Single Run with 11KV 3x185sqmm UG | Electrical work | Lay-SR 11KV 3x185sqmm UG | As per relevent standard specification | 465.46 | M | 23273
15 | Raising of Single Run with 11KV 3x185sqmm UG Cb on support | Electrical work | Raise-SR 11KV 3x185sqmm UG Cb on support | As per relevent standard specification | 126.23 | M | 1893.45
377.6 | Laying of earth mat,excavation 75x 8mm | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 24544
416 | Laying of earth mat,excavation 25x3mm including material | Electrical work | Laying of earth mat,excavation 25x3mm | As per relevent standard specification | 68 | RMT | 28288
16 | Loading of 11 KV VCBs along with Panel boards | Electrical work | LOADING of 11 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 16384
16 | Un loading of 11 KV VCBs along with Panel boards | Electrical work | UNLOADING of 11 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 16711.68
16 | Erection of 11KV indoor switch gear panel/indoor PT panel / Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Electrical work | Erection of 11KV indoor switchgear panel | As per relevent standard specification | 8894 | EA | 142304
1 | LOADING AND UN LOADING of 11 KV AB SWCH Con 200/400 A | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 80
1 | Un loading of 11KV AB Switch Conventional type | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 80
1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv TT type AB switch | As per relevent standard specification | 1813.49 | EA | 1813.49
1 | Loading of 11 KV HG Fuse Sets | Electrical work | LOADING of 11 KV HG Fuse Sets | As per relevent standard specification | 18 | EA | 18
1 | Un loading of 11 KV HG Fuse Sets | Electrical work | UNLOADING of 11 KV HG Fuse Sets | As per relevent standard specification | 18 | EA | 18
1 | Erection of 11 KV HG Fuse set including earthing | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
1 | Loading of 220 V Batterry with charger | Electrical work | Loading 220 V Battery with Charger | As per relevent standard specification | 1612 | SET | 1612
1 | Un loading of 220 V Batterry with charger | Electrical work | Un-loading 220 V Battery with Charger | As per relevent standard specification | 1024 | SET | 1024
1 | Erection of 220V Batery with Chrgr incl all-SS | Electrical work | Erect-220V Batery with Chrgr incl all-SS | As per relevent standard specification | 6442.58 | EA | 6442.58
2 | Fabrication and laying of ladder in cable trench | Electrical work | Fab & laying of ladder in cable trench | As per relevent standard specification | 788 | EA | 1576
6 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 7608
2.05 | Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 4471.05
2.05 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 1744.55
2.05 | (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 2650.65
2.05 | (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 988.1
1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 142
2 | Transport of 8MVA Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) | Electrical work | Transport of 8MVA power | As per relevent standard specification | 21945 | EA | 43890
2 | Loading of 8MVA PTR | Electrical work | LOADING of 8 MVA PTR | As per relevent standard specification | 5805.84 | EA | 11611.68
2 | Unloading of 8MVA PTR | Electrical work | UNLOADING of 8 MVA PTR | As per relevent standard specification | 5805.84 | EA | 11611.68
2 | Erection of 8 MVA PTR. | Electrical work | Erec 33/11 KV, 8 MVA PTR as per Spec | As per relevent standard specification | 49480.2 | EA | 98960.4
26 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 32089.2
26 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 10036
2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 2468.4
12 | Transport of Above 10 Km and upto 20 Km with Lorry for each trip conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Electrical work | Transport of Cond Drum,VCBs >10 & <20Km | As per relevent standard specification | 3299.7 | EA | 39596.4
2.05 | FabricationofMainandAuxiliarystructureswithpowerdrillingusingraw steel suchasM.S.Angles, Plates, Channels, R.S.Joists, including the supplyandfabricationof6mmbaseandtopplateforBoxpoletotheRS Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Electrical work | Fabrication of struc.with power drilling | As per relevent standard specification | 6852 | TO | 14046.6
150 | Laying of Double Run with 33KV 3x400sqmm UG Cb HG/BC/CC/BT | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 751.16 | M | 112674
150 | Laying of Double Run with 11KV 3x400sqmm UG Cb HG/BC/CC/BT | Electrical work | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 631.06 | M | 94659
4 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 11059.04
4 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 11kv 3x300 xlpe | As per relevent standard specification | 2370.63 | EA | 9482.52
2 | Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 11kv 3x185 xlpe | As per relevent standard specification | 2370.63 | EA | 4741.26
3 | Erection of 9/10/11Meter Box pole | Electrical work | Erection of 9/10/11Meter Box pole | As per relevent standard specification | 2643.83 | EA | 7931.49
6 | Loading of R.S. Joists 175 x 85 mm | Electrical work | LOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 76 | EA | 456
6 | Un loading of R.S. Joists 175 x 85 mm | Electrical work | UNLOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 50 | EA | 300
6 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical work | Painting of RS Joist(1C RO, 2C Al.Paint) | As per relevent standard specification | 1132 | EA | 6792
1.75 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 386.75
1.75 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 323.75
3.25 | Transport of ABOVE 10KM upto 20km iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading | Electrical work | TRANSPORT OF STEEL 10 TO 20KM | As per relevent standard specification | 412.08 | TO | 1339.26
0.279 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 1086.147
9.27 | Earth work excavation of in all soils except hard rock requiring blasting | Electrical work | Excavate-Pit in Soil except Hrd Rck | As per relevent standard specification | 345 | M3 | 3198.15
300 | Laying of 2nd cable in excavated trench | Electrical work | Lay-2nd Cable in Excavated Trench Cb HG/BC/CC/BT | As per relevent standard specification | 204.1 | M | 61230
2.6 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Electrical work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 1989
38 | Excavation of pits size 0.92 M x 0.92M x 2.3M( in hard rock not requiring blasting. (In hard murram / rock boulders) | Electrical work | Exc of Hard pit w/o blast 0.92X0.92X2.3M | As per relevent standard specification | 1308.15 | EA | 49709.7
38 | Erection of spun pole 12.5 Mtrs in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erection of Spun pole 12.5Mt | As per relevent standard specification | 4115.7 | EA | 156396.6
12 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Electrical work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 7200
12 | Erection of 9.1 M long PSCC poles for Strut in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 28800
27.6 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting | Electrical work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 14352
5.75 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 10117.125
2.3 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 28980.138
300 | Laying of Double Run with 33KV 3x400sqmm UG Cb HG/BC/CC/BT | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 751.16 | M | 225348
300 | Laying of 2nd cable in excavated trench | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 61230
120 | Raising of double run with 33KV 3x400sqmm UG Cb on support | Electrical work | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 323.85 | M | 38862
28.856 | Concreting the location after erection of 12.5Mtrs/11 Mtrs pole/9.1 Mtrs poles with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. ,17 No's 12.5 mtr spun poles (0.75x0.9x1.95mtrs)*17 = 22.37 cu mtr and 12 No's 9.1 mtr poles (0.6x0.6x1.5mtrs)*12 = 6.48 cu mtr. | Electrical work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 189843.624
2 | loading of 11KV/33KV XLPE UG Cable for all size | Electrical work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | EA | 2048
2 | Un loading of 11KV/33KV XLPE UG Cable for all size | Electrical work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | EA | 2048
4 | LOADING OF 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | Electrical work | Loading 11/33KV Straight thr jointkit | As per relevent standard specification | 8 | EA | 32
4 | UN LOADING OF 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | Electrical work | Un-loading 11/33KV Straight thr jointkit | As per relevent standard specification | 4 | EA | 16
8 | Loading of 33/11KV XLPE UG Cable End Termination Kits for all size | Electrical work | Loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 6 | EA | 48
8 | UN Loading of 33/11KV XLPE UG Cable End Termination Kits for all size | Electrical work | Un-loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 4 | EA | 32
60 | S-GI Bolts & Nuts,Washers etc., | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 7050
38 | Sub Transport of 11/12.5/12.9M Spun poles (Including loading and unloading) upto 10KM | Electrical work | SubTrnsprt any Spun Pole incl. L&UL<10KM | As per relevent standard specification | 771.38 | EA | 29312.44
12 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 4887.48
2 | LOADING of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
2 | UNLOADING of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
2 | Transport of Cond Drum,VCBs upto 10Km | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
1.925 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 1187.9175
1.925 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 425.425
1.925 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 356.125
16 | LOADING of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 48
16 | UNLOADING of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 48
30 | Load of 11KV Polymer Pin Insulator-GI pin | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 30
30 | Unload of 11KV Polymer Pin Insulator-GI pin | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 30
5 | LOADING of 33 & 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 10
5 | UNLOADING of 33 & 11 KV Disc insulator | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 10
2 | LOADING of 33KV Metal parts-bag of 25no | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
2 | UNLOADING of 33 KV Metal parts-bagof 25 | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
2 | LOADING of 11 KV Metal parts | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 96
2 | UNLOADING of 11 KV Metal parts Bag | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 96
38 | Fabrication of Back clamps with 75 x 8 mm MS Flatincluding 2 coats of Red oxide painting | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 1178
24 | Fabrication of STAY clamps with 75 x 8 mm MS Flatincluding 2 coats of Red oxide painting | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 1008
10 | Fabrication of Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 150
38 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 1216
28 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 19166.84
6 | Supply of Galvanised M+3 Tower as per ASCI Standard. Supply of Galvanised M+3 type tower as per Specification. i.e. 1.34 MT per each tower including the following terms. Supply of Suitable Hot dip Galvanised, Zinc coated Nuts and bolts with suitable plain and spring washers of 158 Kgs per each M+3 tower. Supply of material for Painting of structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 litres of thinner 1st coat is to be applied before erection of tower and 2nd coat after stringing. Supply of material for 2 nos. Pipe earthing of towers with 40mm dia GI pipe, including cost of pipe, bentonite powder and running of GI flat etc., per each tower. | Electrical work | S-M+3 Tower GALV | As per relevent standard specification | 140674.3 | EA | 844045.8
14 | Supply of extension of 3mtrs for M+3 Tower as per ASCI Standard. Supply of Galvanised M+3 type tower as per Specification @ 0.33 MT per each M+3 tower. Supply of Suitable Hot dip Galvanised, Zinc coated Nuts and bolts with suitable plain and spring washers @ 30.23 Kgs per each tower. Supply of material for Painting of structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 litres of thinner 1st coat is to be applied before erection of tower and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Electrical work | S-Mat. for Extn of M+3 Tower by 3M GALV | As per relevent standard specification | 28520.64 | EA | 399288.96
6 | Erection of M+3 Tower, as per the following terms: Fabrication of tower Parts as per Specification @ 1.34 MT per each M+3 Tower . Setting of stubs in position for laying of foundation of towers with 1:2:4 cc mix using 40 mm HBG metal including cost of all concreting materials, form boxes and cement and curing for 14 days (40 mm HBG metal for pyramid portion and 20 mm HBG metal for concreting per each tower . Erection of tower parts completely as per specifications including erection of insulators with all accessories, jumpering,transport of meterial and bolts and nuts etc., Tack welding of total tower nuts and bolts . Including labour for Pipe earthing of towers with 40mm dia GI pipe, including cost of pipe, bentonite powder and running of GI flat etc., Transport of Material to site including loading and unloading. Labour charges for painting including scratching and cleaning of tower parts. | Electrical work | Erect- M+3 Tower GALV | As per relevent standard specification | 64576 | EA | 387456
14 | Erection of 3M extension for tower parts completely as per specifications including erection of insulators with all accessories, jumpering,transport of meterial and bolts and nuts etc., Transport of Material to site including loading and unloading. Labour charges for painting including scratching and cleaning of tower . | Electrical work | Erect-Extn of 3M for M+3 Tower GALV | As per relevent standard specification | 5168.95 | EA | 72365.3
6 | Excavation of pits Size (1.2M x 1.2M x 3.3M ) 4.752cum in all soils except hard rock requiring blasting | Electrical work | Excvt Pit ext HardBlst 1.2Mx1.2Mx3.3M | As per relevent standard specification | 1997.93 | EA | 11987.58
10 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Electrical work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 7650
80 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra ea | Electrical work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 56000
60 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Electrical work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 100800
35 | 8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Electrical work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 21000
140 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit exc | Electrical work | Erection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 583139.2
35 | Erection of 9.1 M long PSCC poles for Strut in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 84000
25 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 33750
58.275 | Concreting the location after erection of 12.5Mtrs/11 Mtrs pole/9.1 Mtrs poles with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. ,35 No's 11 mtr poles (0.75x0.75x2mtrs)*35 = 39.375 cu mtr and 35 No's 9.1 mtr poles (0.6x0.6x1.5mtrs)*35 = 18.9 cu mtr. | Electrical work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 383391.225
4 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 34000
3 | Paving of the 55 sqmm AAA conductor and stringing for 6 conductor duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 6 Cond | As per relevent standard specification | 16000 | KM | 48000
250 | S-GI Bolts & Nuts,Washers etc., | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 29375
10.19 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2251.99
10.19 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1885.15
10.19 | TRANSPORT OF STEEL 30 TO 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 5986.8288
600 | Load of 11KV Polymer Pin Insulator-GI pin | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 600
600 | Unload of 11KV Polymer Pin Insulator-GI pin | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 600
4 | Transport of Cond Drum,VCBs >20 & <30Km | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 14765.52
4 | LOADING of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 808
4 | UNLOADING of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 400
480 | Laying of 11 KV 3x300 Sqmm Cable Along the CC / BT multi layer road requiring compressor including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) | Electrical work | Lay-DR 11KV 3x300sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1264.64 | M | 607027.2
480 | Laying of 2nd cable in excavated trench | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 97968
120 | Raising of 11 KV 3x300 Sqmm Cable double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical work | Raise-DR 11KV 3x300sqmm UG Cb on support | As per relevent standard specification | 275.4 | M | 33048
4 | loading of 11KV/33KV XLPE UG Cable for all size | Electrical work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | EA | 4096
4 | Un loading of 11KV/33KV XLPE UG Cable for all size | Electrical work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | EA | 4096
5 | LOADING OF 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | Electrical work | Loading 11/33KV Straight thr jointkit | As per relevent standard specification | 8 | EA | 40
5 | UN LOADING OF 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | Electrical work | Un-loading 11/33KV Straight thr jointkit | As per relevent standard specification | 4 | EA | 20
12 | Loading of 33/11KV XLPE UG Cable End Termination Kits for all size | Electrical work | Loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 6 | EA | 72
12 | UN Loading of 33/11KV XLPE UG Cable End Termination Kits for all size | Electrical work | Un-loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 4 | EA | 48
140 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 60475.8
35 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 14255.15
260 | LOADING of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 1040
260 | UNLOADING of 11 KV V -Cross arms | Electrical work | UNLOADING of 11 KV V -Cross arms | As per relevent standard specification | 4 | EA | 1040
15 | LOADING of 11 KV Metal parts | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 720
15 | UNLOADING of 11 KV Metal parts Bag | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 720
80 | LOADING of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 80
80 | UNLOADING of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 80
15 | LOADING of 33 & 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 30
15 | UNLOADING of 33 & 11 KV Disc insulator | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 30
120 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 72822
120 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting | Electrical work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 62400
70 | Fabrication of back clamps with 50 x6 mm MS Flatincluding 2 coats of Red oxide painting | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 1050
120 | Fabrication of STAY clamps with 50 x6 mm MS Flatincluding 2 coats of Red oxide painting | Electrical work | Fab Stay clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 25 | EA | 3000
140 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 4480
2 | Supply of Galvanised M+3 Tower as per ASCI Standard. Supply of Galvanised M+3 type tower as per Specification. i.e. 1.34 MT per each tower including the following terms. Supply of Suitable Hot dip Galvanised, Zinc coated Nuts and bolts with suitable plain and spring washers of 158 Kgs per each M+3 tower. Supply of material for Painting of structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 litres of thinner 1st coat is to be applied before erection of tower and 2nd coat after stringing. Supply of material for 2 nos. Pipe earthing of towers with 40mm dia GI pipe, including cost of pipe, bentonite powder and running of GI flat etc., per each tower. | Electrical work | S-M+3 Tower GALV | As per relevent standard specification | 140674.3 | EA | 281348.6
6 | Supply of extension of 3mtrs for M+3 Tower as per ASCI Standard. Supply of Galvanised M+3 type tower as per Specification @ 0.33 MT per each M+3 tower. Supply of Suitable Hot dip Galvanised, Zinc coated Nuts and bolts with suitable plain and spring washers @ 30.23 Kgs per each tower. Supply of material for Painting of structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 litres of thinner 1st coat is to be applied before erection of tower and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Electrical work | S-Mat. for Extn of M+3 Tower by 3M GALV | As per relevent standard specification | 28520.64 | EA | 171123.84
2 | Erection of M+3 Tower, as per the following terms: Fabrication of tower Parts as per Specification @ 1.34 MT per each M+3 Tower . Setting of stubs in position for laying of foundation of towers with 1:2:4 cc mix using 40 mm HBG metal including cost of all concreting materials, form boxes and cement and curing for 14 days (40 mm HBG metal for pyramid portion and 20 mm HBG metal for concreting per each tower . Erection of tower parts completely as per specifications including erection of insulators with all accessories, jumpering,transport of meterial and bolts and nuts etc., Tack welding of total tower nuts and bolts . Including labour for Pipe earthing of towers with 40mm dia GI pipe, including cost of pipe, bentonite powder and running of GI flat etc., Transport of Material to site including loading and unloading. Labour charges for painting including scratching and cleaning of tower parts. | Electrical work | Erect- M+3 Tower GALV | As per relevent standard specification | 64576 | EA | 129152
6 | Erection of 3M extension for tower parts completely as per specifications including erection of insulators with all accessories, jumpering,transport of meterial and bolts and nuts etc., Transport of Material to site including loading and unloading. Labour charges for painting including scratching and cleaning of tower . | Electrical work | Erect-Extn of 3M for M+3 Tower GALV | As per relevent standard specification | 5168.95 | EA | 31013.7
2 | Excavation of pits Size (1.2M x 1.2M x 3.3M ) 4.752cum in all soils except hard rock requiring blasting | Electrical work | Excvt Pit ext HardBlst 1.2Mx1.2Mx3.3M | As per relevent standard specification | 1997.93 | EA | 3995.86
1 | Erection of 33 KV AB Switch including alignment and earthing | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 4500
2 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra ea | Electrical work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 1400
2 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit exc | Electrical work | Erection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 8330.56
4 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 9600
4.274 | Concreting the location after erection of 12.5Mtrs/11 Mtrs pole/9.1 Mtrs poles with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. ,2 No's 11 mtr poles (0.75x0.75x2mtrs)*2 = 2.25 cu mtr and 4 No's 9.1 mtr poles (0.6x0.6x1.5mtrs)*4 = 2.16 cu mtr. | Electrical work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28118.646
5 | S-GI Bolts & Nuts,Washers etc., | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 587.5
0.336 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 74.256
0.336 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 62.16
0.336 | TRANSPORT OF STEEL 30 TO 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 197.4067
2 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 863.94
4 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 1629.16
1 | LOADING of 11 KV Metal parts | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 48
1 | UNLOADING of 11 KV Metal parts Bag | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 48
1 | LOADING of 33 & 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 2
1 | UNLOADING of 33 & 11 KV Disc insulator | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 2
2 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 6972
2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 2468.4
30 | Supply of Earthing GI flat 25x3 mm incl material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 3150
1 | LOADING of 33 KV AB SWCH Con 400/800 A | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 126
1 | UN LOADING of 33 KV AB SWCH Con 400/800 A | Electrical work | UN LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 79
60 | Hire-JCB to Level & Clear the Site | Machinery | Hire-JCB to Level & Clear the Site | As per relevant standard specification | 2164.1 | H | 129846
441.21 | Excavation in Ordinary Soil | Earth work | Excavation in Ordinary Soil | As per relevant standard specification | 347 | M3 | 153099.87
74.58 | PCC with 40mm Metal (1:4:8) | Concrete | PCC with 40mm Metal (1:4:8) | As per relevant standard specification | 4084 | M3 | 304584.72
24.3 | PCC with 40mm Metal (1:3:6) | Concrete | PCC with 40mm Metal (1:3:6) | As per relevant standard specification | 4391 | M3 | 106701.3
11.95 | PCC with 20mm Metal (1:2:4) | Concrete | PCC with 20mm Metal (1:2:4) | As per relevant standard specification | 5524 | M3 | 66011.8
30.25 | RCC Footing: M20Gr, Steel Centering | RCC | RCC Footing: M20Gr, Steel Centering | As per relevant standard specification | 8247 | M3 | 249471.75
15.76 | RCC Column GF: M20Gr, Steel Centering | RCC | RCC Column GF: M20Gr, Steel Centering | As per relevant standard specification | 10942 | M3 | 172445.92
5.52 | RCC Plinth Beam: M20Gr, Steel Centering | RCC | RCC Plinth Beam: M20Gr, Steel Centering | As per relevant standard specification | 10667 | M3 | 58881.84
14.32 | RCC Lintel GF: M20Gr, Steel Centering | RCC | RCC Lintel GF: M20Gr, Steel Centering | As per relevant standard specification | 11102 | M3 | 158980.64
2.35 | RCC Sunshade GF: M20Gr, Steel Centering | RCC | RCC Sunshade GF: M20Gr, Steel Centering | As per relevant standard specification | 1164 | M2 | 2735.4
7.43 | RCC Roof Beam GF: M20Gr, Steel Centering | RCC | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevant standard specification | 10677 | M2 | 79330.11
36.87 | RCC Roof Slab GF: M20Gr, Steel Centering | RCC | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevant standard specification | 10228 | M3 | 377106.36
14.2 | Reinforcement Steel Fe 415/500 | Steel | Reinforcement Steel Fe 415/500 | As per relevant standard specification | 74027 | TO | 1051183.4
252.27 | CRS Masonary CM(1:6) 2nd Sort | Masonry | CRS Masonary CM(1:6) 2nd Sort | As per relevant standard specification | 4451 | M3 | 1122853.77
196.35 | Raised Pointing to CRS Masonary CM(1:3) | Plastering | Raised Pointing to CRS Masonary CM(1:3) | As per relevant standard specification | 94 | M2 | 18456.9
128.416 | Brick Masonary in CM(1:6) GFloor | Masonry | Brick Masonary in CM(1:6) GFloor | As per relevant standard specification | 7633 | M3 | 980199.328
394.2 | S&Filling with Borrowed Gravel | Gravel | S&Filling with Borrowed Gravel | As per relevant standard specification | 435 | M3 | 171477
2286.8985 | Plastering 20mm (16mm+4mm)GFloor | Plastering | Plastering 20mm (16mm+4mm)GFloor | As per relevant standard specification | 411 | M2 | 939915.2835
228 | Impervious Coat 20mm CM(1:3) GFloor | Plastering | Impervious Coat 20mm CM(1:3) GFloor | As per relevant standard specification | 441 | M2 | 100548
52.56 | RCM Drop Wall 40mm CM(1:2) Gfloor | Plastering | RCM Drop Wall 40mm CM(1:2) Gfloor | As per relevant standard specification | 2447 | M2 | 128614.32
17.28 | S&F Aluminium Window | Windows | S&F Aluminium Window | As per relevant standard specification | 3381.54 | M2 | 58433.0112
18.75 | S&F of MS Safety Grill | MS grills | S&F of MS Safety Grill | As per relevant standard specification | 2539 | M2 | 47606.25
9.3 | S&F Collapsible steel shutter | MS Shutter | S&F Collapsible steel shutter | As per relevant standard specification | 4017 | M2 | 37358.1
5.04 | S&F MT Wood Frame & Door-Laminate | Doors | S&F MT Wood Frame & Door-Laminate | As per relevant standard specification | 6799.02 | M2 | 34267.0608
26.8 | Ceramic tile Flooring 20 mm CM (1:3) | Tiles | Ceramic tile Flooring 20 mm CM (1:3) | As per relevant standard specification | 734 | M2 | 19671.2
137.53 | Polished Shabad Flooring 20mm CM(1:3) | Shabad floor | Polished Shabad Flooring 20mm CM(1:3) | As per relevant standard specification | 660 | M2 | 90769.8
10.4 | Polished Shabad Skirting CM(1:3) | Shabad floor | Polished Shabad Skirting CM(1:3) | As per relevant standard specification | 727 | M2 | 7560.8
582.37 | Painting with OBD 2Coats+Primer | Painting | Painting with OBD 2Coats+Primer | As per relevant standard specification | 109.9 | M2 | 64002.463
1095.093 | Painting SnowCem/Apex 2 Coats+Primer | Painting | Painting SnowCem/Apex 2 Coats+Primer | As per relevant standard specification | 195.91 | M3 | 214539.6696
40.26 | S&F Aliminium Double Leaf Door | Aluminium door | S&F Aliminium Double Leaf Door | As per relevant standard specification | 5996.4 | M2 | 241415.064
4746 | S&F structural Steel Angles etc., | Steel | S&F structural Steel Angles etc., | As per relevant standard specification | 104 | Kg | 493584
47.54 | S&F of MS gate | Ms gate | S&F of MS gate | As per relevant standard specification | 4579.89 | M2 | 217727.9706
90 | S&F Surfc pvc pipe 25mm dia. 1.5mmthk | Electrification | S&F Surfc pvc pipe 25mm dia. 1.5mmthk | As per relevant standard specification | 83 | M | 7470
90 | S&F Conceal pvc pipe 25mm dia. in wall | Electrification | S&F Conceal pvc pipe 25mm dia. in wall | As per relevant standard specification | 89 | M | 8010
2 | S&F 8wySPN DB IP-42 | Electrification | S&F 8wySPN DB IP-42 | As per relevant standard specification | 5624 | EA | 11248
10 | S&F Modular 3pin 6A sockets | Electrification | S&F Modular 3pin 6A sockets | As per relevant standard specification | 276 | EA | 2760
4 | S&F Modular 3pin 16/6A sockets | Electrification | S&F Modular 3pin 16/6A sockets | As per relevant standard specification | 437 | EA | 1748
44 | S&F Flush type switch LP,FP,EFP RBuild | Electrification | S&F Flush type switch LP,FP,EFP RBuild | As per relevant standard specification | 487 | EA | 21428
20 | S&F 20W LED Tubelight Batten | Electrification | S&F 20W LED Tubelight Batten | As per relevant standard specification | 531 | EA | 10620
4 | S&F 12" light duty exhaust fan | Electrification | S&F 12" light duty exhaust fan | As per relevant standard specification | 2068 | EA | 8272
360 | S&R 2 of 22/0.3mm (1.5 sq.mm) (FR) | Electrification | S&R 2 of 22/0.3mm (1.5 sq.mm) (FR) | As per relevant standard specification | 67 | Rmt | 24120
270 | S&R 2 of 36/0.3mm (2.5 sq.mm) (FR) | Electrification | S&R 2 of 36/0.3mm (2.5 sq.mm) (FR) | As per relevant standard specification | 95 | Rmt | 25650
15 | S&F Batten Holder | Electrification | S&F Batten Holder | As per relevant standard specification | 116 | EA | 1740
10 | S&F of 1200mm (48'') sweep Ceiling fan | Electrification | S&F of 1200mm (48'') sweep Ceiling fan | As per relevant standard specification | 2215 | EA | 22150
1 | Providing independent Earthing | Electrification | Providing independent Earthing | As per relevant standard specification | 4891 | EA | 4891
12 | S&F 152.4mm SWG SP-1 pipes -3ft depth | Plumbing | S&F 152.4mm SWG SP-1 pipes -3ft depth | As per relevant standard specification | 763 | Rmt | 9156
2 | Cnstrn. Of 1'6"x1'6" brick CHAMBERS | Plumbing | Cnstrn. Of 1'6"x1'6" brick CHAMBERS | As per relevant standard specification | 4610 | EA | 9220
2 | S&F 90mm dia Door Bend PVC/SWR pipe | Plumbing | S&F 90mm dia Door Bend PVC/SWR pipe | As per relevant standard specification | 113 | EA | 226
2 | S&F 90mm dia Plain Bend PVC/SWR pipe | Plumbing | S&F 90mm dia Plain Bend PVC/SWR pipe | As per relevant standard specification | 84 | EA | 168
6 | S&F 110mm dia 3M 1socket PVC/SWR pipe | Plumbing | S&F 110mm dia 3M 1socket PVC/SWR pipe | As per relevant standard specification | 422 | Rmt | 2532
6 | S&F 90mm dia 3M 1socket PVC/SWR pipe | Plumbing | S&F 90mm dia 3M 1socket PVC/SWR pipe | As per relevant standard specification | 370.67 | Rmt | 2224.02
1 | S&F 150 mm x 100 mm SWG gully trap | Plumbing | S&F 150 mm x 100 mm SWG gully trap | As per relevant standard specification | 749 | Ea | 749
1 | S&F European Water Closet of 1st quality | Plumbing | S&F European Water Closet of 1st quality | As per relevant standard specification | 2081 | EA | 2081
1 | S&F Indian make plastic seat and lid | Plumbing | S&F Indian make plastic seat and lid | As per relevant standard specification | 1280 | EA | 1280
2 | S&F 12.7mm stop cock 400 grams | Plumbing | S&F 12.7mm stop cock 400 grams | As per relevant standard specification | 669 | EA | 1338
5 | S&F 12.7mm bib tap 400 grams | Plumbing | S&F 12.7mm bib tap 400 grams | As per relevant standard specification | 271 | EA | 1355
1 | S&F Flat Back Wash Hand Basin | Plumbing | S&F Flat Back Wash Hand Basin | As per relevant standard specification | 1508 | EA | 1508
3 | S&F 38.1 mm C.P waste coupling | Plumbing | S&F 38.1 mm C.P waste coupling | As per relevant standard specification | 257 | EA | 771
3 | S&F 31.75mm PVC flexible waste pipe 0.9m | Plumbing | S&F 31.75mm PVC flexible waste pipe 0.9m | As per relevant standard specification | 33 | EA | 99
3 | S&F 101.6 mm Nahany Trap | Plumbing | S&F 101.6 mm Nahany Trap | As per relevant standard specification | 134 | EA | 402
1 | S&F porcelain flushing tank 10 Lit | Plumbing | S&F porcelain flushing tank 10 Lit | As per relevant standard specification | 3137 | EA | 3137
1000 | S&F Polyethylene water storage tank | Plumbing | S&F Polyethylene water storage tank | As per relevant standard specification | 10 | L | 10000
5 | S&F15.90mm OD CPVC Pipe - SDR 11 | Plumbing | S&F15.90mm OD CPVC Pipe - SDR 11 | As per relevant standard specification | 239 | Rmt | 1195
60 | S&F 22.20mm OD CPVC Pipe - SDR 11 | Plumbing | S&F 22.20mm OD CPVC Pipe - SDR 11 | As per relevant standard specification | 313 | Rmt | 18780
35 | S&F 28.60mm OD CPVC Pipe - SDR 11 | Plumbing | S&F 28.60mm OD CPVC Pipe - SDR 11 | As per relevant standard specification | 410 | Rmt | 14350
1 | S&F 25mm GM Ball valve | Plumbing | S&F 25mm GM Ball valve | As per relevant standard specification | 466 | EA | 466
1 | S&F 20mm GM Ball valve | Plumbing | S&F 20mm GM Ball valve | As per relevant standard specification | 331 | EA | 331
1 | S&Fsteel towel rod of 600 mm long | Plumbing | S&Fsteel towel rod of 600 mm long | As per relevant standard specification | 437 | EA | 437
1 | S&F CP brass soap dish | Plumbing | S&F CP brass soap dish | As per relevant standard specification | 623 | EA | 623
1 | Geophysical Investgation Charges | Bore well | Geophysical Investgation Charges | As per relevant standard specification | 5000 | EA | 5000
90 | Drilling-165mm Bore Well 0 to 90M | Bore well | Drilling-165mm Bore Well 0 to 90M | As per relevant standard specification | 336 | M | 30240
30 | Drill-165mm Bore Well 90M to 120M | Bore well | Drill-165mm Bore Well 90M to 120M | As per relevant standard specification | 369 | M | 11070
30 | Drill-165mm Bore Well 120M to 150M | Bore well | Drill-165mm Bore Well 120M to 150M | As per relevant standard specification | 394 | M | 11820
30 | S&F 160mm dia PVC Casing | Bore well | S&F 160mm dia PVC Casing | As per relevant standard specification | 844 | M | 25320
1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Bore well | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevant standard specification | 34237 | M | 34237
175 | S&F HDPE Pipe 40mm dia 6kg/sqcm | Bore well | S&F HDPE Pipe 40mm dia 6kg/sqcm | As per relevant standard specification | 160 | EA | 28000
1 | S&E D.O.L Starter 250V Single Phase | Bore well | S&E D.O.L Starter 250V Single Phase | As per relevant standard specification | 1040 | Rmt | 1040
200 | S&R 3C 2.5sqmm Flat Copper Cable | Bore well | S&R 3C 2.5sqmm Flat Copper Cable | As per relevant standard specification | 190 | EA | 38000
2.21 | S&F poly vinyl acrylic board | Name board | S&F poly vinyl acrylic board | As per relevant standard specification | 1930.48 | EA | 4266.3608
3 | Prov supply of electricity to the site | Power supply | Prov supply of electricity to the site | As per relevant standard specification | 5677.88 | M2 | 17033.64
7358.7456 | Provd 2Sets of Structural Drawings | Drawings | Provd 2Sets of Structural Drawings | As per relevant standard specification | 4.5 | M2 | 33114.3552
264.5 | Seigniorage Charges - Sand | Seigniorages | Seigniorage Charges - Sand | As per relevant standard specification | 40 | M3 | 10580
468.7 | Seigniorage Charges - Metal | Seigniorages | Seigniorage Charges - Metal | As per relevant standard specification | 97.5 | M2 | 45698.25
394.2 | Seigniorage Charges - Gravel | Seigniorages | Seigniorage Charges - Gravel | As per relevant standard specification | 30 | M3 | 11826
15771187.3