## Farooq Nagar
SCHEDULE
Name of the Work :- Erection of 33/11KV Indoor SS with 2Nos 8MVA PTRs Construction of control room, compound wall along with MS gate and bore well, cable trenches, power transformer plinths, toilet block, electrification, sanitary and water supply arrangements for the proposed 33/11 KV Indoor Sub-station at Farooq Nagar, Falaknuma in Bahadurpura Constituency in Operation Hyderabad South Circle in Master Plan Circle, Hyderabad
WBS Num: S-1764-12-02-02-03-001 ( Elect) & S-1764-12-07-01-02-001 ( Civil)
Sl No | Estimate Qty | Description of item | Work Type | Item Short Description | APSS / Month Cl.Number | Rate (INR) | UOM | Amount
1 | 2 | LOADING of 8 MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) - 8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
3 | 2 | UNLOADING of 8 MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
4 | 2 | Erection of 8 MVA PTR | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
5 | 1 | LOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10195 | 350 | EA | 350
6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
7 | 1 | UNLOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10513 | 280 | EA | 280
8 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
9 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc - 3 Phase DTRs 63,75 & 100 KVA | Elect | Labour | SWR20905 | 1650 | EA | 1650
10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging .Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification | Elect | Supply | SMR40045 | 42000 | EA | 42000
23 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
24 | 8 | LOADING of RSJoists150 x 150 mm/RailPole | Elect | Labour | SWR10205 | 176 | EA | 1408
25 | 8 | UNLOADING of RSJoists150 x150 mm/RailPol | Elect | Labour | SWR10523 | 107 | EA | 856
26 | 0.83 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 183.43
27 | 0.83 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 153.55
28 | 3.83 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1578.2664
29 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
30 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
31 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
32 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
33 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
34 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
35 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 1846.06
36 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
37 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
38 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
39 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
40 | 3.4 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 751.4
41 | 3.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 629
42 | 3.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1401.072
43 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
44 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
45 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
46 | 314 | Paint-Black to all Earth Flat incl. Paint cost | Elect | Labour | SWR12217 | 55 | M | 17270
47 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
48 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
49 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench withearth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
50 | 56 | Raise-33KV 33KV 630sqmm UG Cb on support | Elect | Labour | SWR12448 | 133 | M | 7448
51 | 106 | Lay-33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
52 | 14 | Raising of 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
53 | 8 | S-33KV 1x630Sqmm GIS ID Unit EndTermtn | Elect | Supply | SMR12473 | 2500 | EA | 20000
54 | 8 | S-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Supply | SMR12474 | 4200 | EA | 33600
55 | 8 | Install-33KV 1x630Sqmm GIS ID EndTermtn | Elect | Labour | SWR12473 | 17600 | EA | 140800
56 | 8 | Install-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Labour | SWR12474 | 4000 | EA | 32000
57 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
58 | 85 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
59 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x185 Sqmm Cable | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
60 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
61 | 90 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
62 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
63 | 2 | Supply of 31/2x185Sqmm UG O/D end term kits | Elect | Supply | SMR40140 | 550 | EA | 1100
64 | 2 | Making of Outdoor/Indoor LT 3 1/2 x 185 Sqmm CableCable End Termination | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
65 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 59400
66 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per pecification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
67 | 6 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 456
68 | 1.6 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 659.328
69 | 6 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 300
70 | 1.6 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
71 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
72 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
73 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
74 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
75 | 5 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
76 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
77 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
78 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 603.415
79 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 240
80 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
81 | 1 | Un loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
82 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
83 | 1 | Loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12406 | 80 | EA | 80
84 | 1 | Un loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12425 | 80 | EA | 80
85 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
86 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
87 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
88 | 18 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
89 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elect | Labour | SWR12125 | 14.03 | M | 420.9
90 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
91 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
92 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
93 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 111304
94 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
95 | 8 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
96 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
97 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 965.464
98 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 384
99 | 8 | S-Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
100 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
101 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
102 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
103 | 400 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 33200
104 | 12 | Sup Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
105 | 1 | Sup Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
106 | 2 | Sup- Trolley mounted CO2 (6.5Kgs) | Elect | Supply | SMR40087 | 9240 | EA | 18480
107 | 2 | Sup Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elect | Supply | SMR40088 | 1386 | SET | 2772
108 | 6 | Sup Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 27720
109 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
110 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
111 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
112 | 1 | Sup Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
113 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
114 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
115 | 1 | Sup Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
116 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
117 | 1 | SupName board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10238 | EA | 10238
118 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
119 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & keycontaining (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23,24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets,6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) AdjustableSpanner 305 mm length least maximum opening 35mmchrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter,(10) Insulated Cutting Plier Length 8” with cable stripperinsulated with thick C. A. sleeve confirming to IS: 4378 - 1990,(11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm,(13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 4925 | SET | 4925
120 | 1 | Sup Rechargeable LED torch light of Standard make | Elect | Supply | SMR40064 | 1733 | EA | 1733
121 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
122 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
123 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
124 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
125 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
126 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | Labour | SWR20032 | 1654 | EA | 1654
127 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | Labour | SWR22090 | 2205 | EA | 2205
128 | 1 | S-10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
129 | 7.5 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 5737.5
130 | 30 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 30720
131 | 15 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 49495.5
132 | 30 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 30720
133 | 4900 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11918 | 572.1 | M | 2803290
134 | 1400 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11927 | 1175.56 | M | 1645784
135 | 200 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (excluding the cost of Hume Pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11936 | 1319.84 | M | 263968
136 | 1000 | Laying of 33KV XLPE UG cable Single Run of Size in Hard Rock (1.2*0.45x1=0.54cum) | Elect | Labour | SWR11003 | 1287 | M | 1287000
137 | 75 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 205875
138 | 30 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 171023.4
139 | 800 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 835200
140 | 300 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 303600
141 | 200 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 25000
142 | 8 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 22118.08
143 | 70 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 9496.2
144 | 7500 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 225000
145 | 75 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 36300
146 | 1.345 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 297.245
147 | 1.345 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 248.825
148 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
149 | 5.845 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2408.6076
150 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
151 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
152 | 18 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 20376
153 | 12 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 11888.16
154 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
155 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
156 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
157 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 74224.278
158 | 0.372 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 1448.196
159 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3340.35
160 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
161 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
162 | 3 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
163 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
164 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
165 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
166 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
167 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | EA | 2640
168 | 6 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
169 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
170 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
171 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
172 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
173 | 8 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 6120
174 | 27 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 27648
175 | 14 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 46195.8
176 | 27 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 27648
177 | 4100 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11919 | 465.46 | M | 1908386
178 | 3100 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 3329214
179 | 200 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (cxcluding the cost of Hume Pipe)-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11937 | 1199.4 | M | 239880
180 | 600 | Laying of 11KV XLPE UG cable Single Run in Hard Rock (1.05*0.45x1=0.4725cum) | Elect | Labour | SWR11005 | 1075 | M | 645000
181 | 80 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 219600
182 | 28 | Making of 11 KV 3x300 Sqmm Cable Straight through joints | Elect | Labour | SWR10386 | 3725.45 | EA | 104312.6
183 | 500 | Supply 4" BClass GI pipe 3.65mm thck 12.2Kg/M | Elect | Supply | SMR40080 | 740 | M | 370000
184 | 500 | Supply 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 379500
185 | 200 | Supply of 4" Hume Pipe | Elect | Supply | SMR40003 | 80 | M | 16000
186 | 16 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
187 | 120 | Raising of Single run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11955 | 144.08 | M | 17289.6
188 | 8000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 240000
189 | 80 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 38720
190 | 0.614 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 135.694
191 | 0.614 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 113.59
192 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
193 | 4.614 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1901.3371
194 | 16 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
195 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
196 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
197 | 8 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
198 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
199 | 160 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6560
200 | 7.521 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 49480.659
201 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 965.464
202 | 0.23 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Elect | Labour | SWR10869 | 3426 | EA | 787.98
203 | 16 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 44624
204 | 16 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 19747.2
205 | 16 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 6176
206 | 8 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 640
207 | 8 | Un loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 640
208 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
209 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
210 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
211 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
212 | 40 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 4700
Electrical total | [7 empty] | 18105681.2011
Civil Portion
213 | 24 | Clearing of site by hiring JCB, complete for the finished item of work. | Civil | Labour | SWR34179 | 2165 | Hrs | 51960
214 | 2 | Providing contour surveying maps with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5665 | EA | 11330
215 | 2 | Providing report on soil bearing capacity | Civil | Labour | SWR34097 | 4500 | EA | 9000
216 | 7500 | Design and submisiion of 2 sets of structural design drawings with soft copy complete finished item of work | Civil | Labour | SWR33426 | 5 | FT2 | 37500
217 | 20.74 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work including seigniorage excluding dewatering charges etc as per SS - 20 B(APSS 308).Hard rock ( blasting prohibited ). | Civil | Labour | SWR33018 | 1440 | Cum | 29865.6
218 | 947 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work excluding dewatering charges etc as per SS - 20B (APSS 308). Ordinary Soil | Civil | Labour | SWR33015 | 486 | Cum | 460242
219 | 108 | Drilling holes in hard granite or sheet rock by Pneumatic compressor 25 mm dia meter etc for complete for item of work | Civil | Labour | SWR34180 | 144 | rmt | 15552
220 | 108 | Grouting the holes with neat cement slurry excluding cost of steel 25 mm dia meter including cost of material labour charges complete fro finished item of work as directed by the engineer in charge | Civil | Labour | SWR34458 | 93 | rmt | 10044
221 | 211.23 | Filling with already available Earthwork in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Civil | Labour | SWR33055 | 202 | Cum | 42668.46
222 | 90.38 | Plain Cement contrete (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4843 | Cum | 437710.34
223 | 82.02 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work. a) Column Footings | Civil | Labour | SWR33098 | 9595 | Cum | 786981.9
224 | 28.46 | RCC M - 20 GF (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. b) Columns" | Civil | Labour | SWR33100 | 13343 | Cum | 379741.78
225 | 4.96 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work c)Plinth Beams | Civil | Labour | SWR33099 | 12465 | Cum | 61826.4
226 | 18.3 | RCC M - 20 GF Beams (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all mater as directed by Engineer incharge of the work. d)Roof Beams" | Civil | Labour | SWR33121 | 12381 | Cum | 226572.3
227 | 1.82 | RCC M - 20 GF Lintels(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Lintels | Civil | Labour | SWR33107 | 13173 | Cum | 23974.86
228 | 43.83 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. / h) Roofslab & Staircase "150mm | Civil | Labour | SWR33128 | 10969 | Cum | 480771.27
229 | 18 | Supplying, fitting and placing HYSD bar reinforcement in foundation complete as per drawings and technical specifications for Bars below 36 mm dia including over laps and wastage, where they are not welded,complete as directed by Engineer incharge of the work. | Civil | Labour | SWR33144 | 75636 | Ton | 1361448
230 | 244 | Coursed rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33041 | 5027 | Cum | 1226588
231 | 87.84 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | Sqm | 10892.16
232 | 99.34 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 8369 | Cum | 831376.46
233 | 345.87 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification as directed by Engineer incharge of the work. | Civil | Labour | SWR33052 | 493 | Cum | 170513.91
234 | 1671.86 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 559 | Sqm | 934569.74
235 | 265.28 | Providng impervious coat to exposed RCC roof slab surface with CM(1:3), 20 mm thick with 1kg of water proof compound per bag of cement laid over roof when it is green including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33156 | 582 | Sqm | 154392.96
236 | 90 | RCM facia 5cm thick in CM (1:3) for drop walls, fins with rabbit wire mesh & nominal reinforcemet as directed by Engineer-in-change with dubara sponge finishing, including cost & conveyance of all materials to site, seigniorage charges, sales & incidental, cost and conveyance of cement, wire mesh, water to work site, centering, scaffolding and form work, lift changes etc., complete for finished items of work but excluding cost of steel & its fabrication charges, for finished item of work. (APSS No.403 & 903). | Civil | Labour | SWR33203 | 3036 | Sqm | 273240
237 | 22.33 | Supply & fixing Aluminimum Anodised Two/Three Track Sliding Windows as per approved drawing with aluminium anodised sections of Series C Jindal sections and outer frame top horizontals & both verticals of 8774 of size 62 x 29.5 mm and bottom horizontal - two track frame of 8773 of size 62 x 29.5 mm, Shutter frame top, bottom and verticals of 8304 of size 50 mm x 20 mm and Weather interlocking frame of 8306 of size 50 x 20 with plain clear float glass 5mm thick fixed including Supply & fixing aluminium handles of 100 mm for each shutter, nylon rollers assembly and all labour charges for fixing the fixtures with required no. of screws, bolts and nuts and includingt labour charges for fixing the frame in position, fixing shutter to frame etc. completed for finished item of work | Civil | Labour | SWR33277 | 3623 | Sqm | 80901.59
238 | 26.68 | Supply & fixing of ms grill to windows with outer frame of ISA2525 of 25mm thick , horizontal and vertical square rods of 10x10mm and paintng with synthetic enamel paint per (0.3 x 1.2 )sqm. | Civil | Labour | SWR33310 | 2990 | sqm | 79773.2
239 | 7.95 | Supplying & fixing collapsible steel shutters with vertical, double channel of 20 x10x2 mm of 100 mm centre ,Bracers with flat iron 40x40x6 mm with 38 mm dia steel pulleys, the top, bottom and side vertical frames of the collapsible gate with 65x65mmx8mm MS Angle and middle guide rail at site height with 65mmx8mm MS flat for the pulleys to guide and fixed with necessary hold fasts, bolts, nuts, rivets, locking arrangements, stoppers, handles, all accessories all fixtures and painted with one coat of approved steel primer etc., complete for finished item of work as per special spn 1105. | Civil | Labour | SWR33411 | 4017 | Sqm | 31935.15
240 | 3.7 | Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood (Schedule Item No. 301.) complete for finished item of work. | Civil | Labour | SWR33269 | 4371 | Sqm | 16172.7
241 | 9.59 | Flooring with cermic tiles of set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33224 | 913 | Sqm | 8755.67
242 | 225.78 | Flooring with polished shahabad stones 20 mmthick set over base coat of CM (1:3) over already laid CC bed /RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth including cost of all materials like cement, sand, and water and flooring stones etc., complete, including seigniorage charges, labour charges for dresing of flooring stones etc., complete for finished item of work . | Civil | Labour | SWR33219 | 785 | Sqm | 177237.3
243 | 12.5 | Decorated white back ground glazed tiles, set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste mixed with pigment of matching shadeto full depth, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33226 | 882 | Sqm | 11025
244 | 18.22 | Providing skirting to internal walls to 15 cm height/risers of steps with ...mm thick polished Shahabad stone length equal to polished stones, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete, including seigniorage charges, etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33236 | 875 | Sqm | 15942.5
245 | 576.18 | Painting to new walls with 2 coats of ready mixed oil bound wahsable distemper of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 911 for internal walls as directed by Engineer incharge of the work | Civil | Labour | SWR33333 | 146 | Sqm | 84122.28
246 | 1526.94 | Painting to new walls with 2 coats of ACE paint external grade of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 912 for external walls as directed by Engineer incharge of the work. | Civil | Labour | SWR33334 | 154 | Sqm | 235148.76
247 | 9.59 | Supplying and fixing Alluminium glazed door cum fixed window or door using anodised alluminium extruded sections and mat finish for frames sites and Handle/knib,locking arrangements and 4.0mm plain glass fixed to the frame with beeding and qasket with all required item of work. | Civil | Labour | SWR33272 | 6162 | Sqm | 59093.58
248 | 21.3 | Plain Cement contrete (1:2:4) Nominal Mix using 20 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33030 | 6212 | Cum | 132315.6
249 | 30.14 | Plain Cement contrete (1:3:6) Nominal Mix using 40 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33029 | 5133 | Cum | 154708.62
250 | 2354.4 | Supply and fabrication of beams,chanales and angles including labour charges complete for the finished item of work. | Civil | Labour | SWR33145 | 128 | Kg | 301363.2
251 | 337 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | Rmt | 36396
252 | 1 | Supply & fixing 4 way TPN Distribution board with IP-42 protection suitable for 3 phase 40A FP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 12Nos as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
253 | 8 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1328
254 | 2 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 898
255 | 64 | Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 43264
256 | 24 | Supply & Fixing of 28W T5 fluorescent tube. Makes : Crompton / Bajaj / Phillips / Surya / Havells with copper choke,starter etc.,incuding 1No 40W tube etc., complete. | Civil | Labour | SWR33558 | 148 | EA | 3552
257 | 1 | Supply of 12" (300mm)ISI, 900 RPM Light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
258 | 186 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | RMT | 13950
259 | 308 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | RMT | 31724
260 | 16 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 2256
261 | 12 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 27324
262 | 12 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 7068
263 | 10 | Supply & Fixing of 12" heavy duty exhaust fan with metal blades etc including all operational, incidental and labour charges etc. complete for the finished item of worK Makes : Crompton / Havells Ventilair-DB / Orient hill air. | Civil | Labour | SWR33573 | 3887 | EA | 38870
264 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
265 | 10 | S&F 20W LED Tubelight Batten | Civil | Labour | SWR33553 | 582 | EA | 5820
266 | 35 | Supplying, laying, jointing and testing 101.4 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | RMT | 26425
267 | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | Civil | Labour | SWR34296 | 8766 | EA | 8766
268 | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 256
269 | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 200
270 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | RMT | 5544
271 | 5 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | RMT | 2050
272 | 2 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 1534
273 | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap | Civil | Labour | SWR34314 | 2228 | EA | 2228
274 | 1 | Supplying and Fixing best Indian make plastic seat and lid for European water closets with rubber or plastic Buffers as per IS 2548-1996 | Civil | Labour | SWR34315 | 1324 | EA | 1324
275 | 2 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 1442
276 | 4 | S&F 15 mm bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 298 | EA | 1192
277 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
278 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
279 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
280 | 1 | Supplying & Fixing low down Plastic flushing tank 10 Lit Capacity Hindustan Sanitary ware/ parry/ Neycer with internal components | Civil | Labour | SWR34376 | 2032 | EA | 2032
281 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
282 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality complete for finished item of work | Civil | Labour | SWR34426 | 33 | EA | 66
283 | 20 | S & F of (15.90mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | RMT | 4780
284 | 50 | Supply and Fixing of (22.20mm) Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | RMT | 15650
285 | 40 | Supply and Fixing of (28.60mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | RMT | 16400
286 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
287 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 331
288 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
289 | 1 | Supply & fixing NP soap dish heavy type with NP screws | Civil | Labour | SWR34429 | 675 | EA | 675
290 | 17.5 | Supply and fixing of AC sheets including cost of material labour conveyence etc complete for finished item of work as directed by the engineer in charge. | Civil | Labour | SWR33400 | 395 | M2 | 6912.5
291 | 3.05 | S&F of Glow sign board size 10' x 3' including lettering, labour charges, fitting charges cost of all materials and complete for finished item. | Civil | Labour | SWR33422 | 3553 | Sqm | 10836.65
292 | 195.02 | Carting away of excavated soils Complete for finished item of work | Civil | Labour | SWR34151 | 270 | Cum | 52655.4
293 | 6.27 | Providing 20 mm chips in the transformer area including cost, lead and labour charges complete for finished item of work | Civil | Labour | SWR33057 | 1525 | Cum | 9561.75
294 | 20.88 | Supply and fixing of MS GATE with redoxide and 2 Coats of Anamil paint Complete finished item of work as directed by Engineer - in-charge | Civil | Labour | SWR33404 | 5299 | sqm | 110643.12
295 | 1 | Geophysical Investgation charges for water point by Geologist as directed by Engineer in chargecomplete for the finished item of work. | Civil | Labour | SWR33608 | 5000 | Sqm | 5000
296 | 185 | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete 0 to 90M | Civil | Labour | SWR33609 | 336 | Rmt | 62160
297 | 25 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | Rmt | 22075
298 | 1 | Supply and erecting, ISI mark submersible 2.0HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33626 | 21619 | EA | 21619
299 | 168 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cSqm including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | Rmt | 30240
300 | 1 | Supply and erecting D.O.L Starter 250V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33644 | 1040 | EA | 1040
301 | 180 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | Rmt | 34560
302 | 1 | Provd-DGPS & Total Staion Survey | Civil | Labour | SWR34506 | 5000 | EA | 5000
303 | 1 | Providing supply of electricity to the site premises through custamer service centre duly applying for new connection including service wire, application complete the work. | Civil | Labour | SWR33425 | 5408 | EA | 5408
304 | 293.24 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | Cum | 11729.6
305 | 563.87 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | Cum | 54977.325
306 | 300 | Seigniorage Charges -Gravel | Civil | Labour | SWR34472 | 30 | Cum | 9000
Civil Total | [7 empty] | 10206468.635 | 10206468.64
Total ( Electr + Civil) | [7 empty] | 28312149.8361 | 18105681.22
18% GST | [7 empty] | 5096186.9705 | 28312149.86 | 0.02388
Grand Total(Electrical + Civil) incl GST | [7 empty] | 33408336.8066 | 33408336.8348
0.028178

## Nizamia Unani
SCHEDULE
Name of the Work :- Erection of 33/11KV Indoor SS with 2Nos 8MVA PTRs along with Construction of control room, compound wall along with MS gate and borewell, cable trenches, power transformer plinths, toilet block, electrification, sanitary and water supply arrangements for the proposed 33/11 KV Indoor Sub-station at Nizamia Unani Hospital, Charminar in in Bahadurpura Constituency in Operation Hyderabad South Circle in Master Plan, Hyderabad Circle
WBS Element :- S-1765-12-02-02-03-001 (Elect) & S-1765-12-07-01-02-001(civil)
Electrical Portion:
Sl No | Estimate QTY | Description of item | Work Type | Item Short Description | APSS / Month Cl.Number | Rate (INR) | UOM | AMOUNT
1 | 2 | LOADING of 8 MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) - 8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
3 | 2 | UNLOADING of 8 MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
4 | 2 | Erection of 8 MVA PTR | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
5 | 1 | LOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10195 | 350 | EA | 350
6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
7 | 1 | UNLOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10513 | 280 | EA | 280
8 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
9 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc - 3 Phase DTRs 63,75 & 100 KVA | Elect | Labour | SWR20905 | 1650 | EA | 1650
10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space)(excluding of loading unloading) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) (excludingof loading unloading)Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging .Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification | Elect | Supply | SMR40045 | 42000 | EA | 42000
23 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
24 | 8 | LOADING of RSJoists150 x 150 mm/RailPole | Elect | Labour | SWR10205 | 176 | EA | 1408
25 | 8 | UNLOADING of RSJoists150 x150 mm/RailPol | Elect | Labour | SWR10523 | 107 | EA | 856
26 | 0.83 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 183.43
27 | 0.83 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 153.55
28 | 3.83 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1578.2664
29 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
30 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
31 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
32 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
33 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
34 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
35 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 1846.06
36 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
37 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
38 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
39 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
40 | 3.4 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 751.4
41 | 3.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 629
42 | 3.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1401.072
43 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
44 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
45 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
46 | 314 | Paint-Black to all Earth Flat incl. Paint cost | Elect | Labour | SWR12217 | 55 | M | 17270
47 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
48 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
49 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench withearth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
50 | 56 | Raise-33KV 33KV 630sqmm UG Cb on support | Elect | Labour | SWR12448 | 133 | M | 7448
51 | 106 | Lay-33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
52 | 14 | Raising of 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
53 | 8 | S-33KV 1x630Sqmm GIS ID Unit EndTermtn | Elect | Supply | SMR12473 | 2500 | EA | 20000
54 | 8 | S-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Supply | SMR12474 | 4200 | EA | 33600
55 | 8 | Install-33KV 1x630Sqmm GIS ID EndTermtn | Elect | Labour | SWR12473 | 17600 | EA | 140800
56 | 8 | Install-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Labour | SWR12474 | 4000 | EA | 32000
57 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
58 | 85 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
59 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x185 Sqmm Cable | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
60 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
61 | 90 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
62 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
63 | 2 | Supply of 31/2x185Sqmm UG O/D end term kits | Elect | Supply | SMR40140 | 550 | EA | 1100
64 | 2 | Making of Outdoor/Indoor LT 3 1/2 x 185 Sqmm CableCable End Termination | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
65 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 59400
66 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per pecification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
67 | 6 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 456
68 | 1.6 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 659.328
69 | 6 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 300
70 | 1.6 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
71 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
72 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
73 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
74 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
75 | 5 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
76 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
77 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
78 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 603.415
79 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 240
80 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
81 | 1 | Un loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
82 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
83 | 1 | Loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12406 | 80 | EA | 80
84 | 1 | Un loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12425 | 80 | EA | 80
85 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
86 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
87 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
88 | 18 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
89 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elect | Labour | SWR12125 | 14.03 | M | 420.9
90 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
91 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
92 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
93 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 111304
94 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
95 | 8 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
96 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
97 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 965.464
98 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 384
99 | 8 | S-Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
100 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
101 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
102 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
103 | 400 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 33200
104 | 12 | Sup Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
105 | 1 | Sup Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
106 | 2 | Sup TrollyMounted Co2 Cylinders(IS-2878) | Elect | Supply | SMR40087 | 9240 | EA | 18480
107 | 2 | Sup Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elect | Supply | SMR40088 | 1386 | SET | 2772
108 | 6 | Sup Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 27720
109 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
110 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
111 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
112 | 1 | Sup Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
113 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
114 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
115 | 1 | Sup Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
116 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
117 | 1 | SupName board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10238 | EA | 10238
118 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
119 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & keycontaining (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23,24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets,6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) AdjustableSpanner 305 mm length least maximum opening 35mmchrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter,(10) Insulated Cutting Plier Length 8” with cable stripperinsulated with thick C. A. sleeve confirming to IS: 4378 - 1990,(11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm,(13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 4925 | SET | 4925
120 | 1 | Sup Rechargeable LED torch light of Standard make | Elect | Supply | SMR40064 | 1733 | EA | 1733
121 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
122 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
123 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
124 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
125 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
126 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | Labour | SWR20032 | 1654 | EA | 1654
127 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | Labour | SWR22090 | 2205 | EA | 2205
128 | 1 | S-10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
129 | 6.5 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 4972.5
130 | 22 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 22528
131 | 11 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 36296.7
132 | 22 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 22528
133 | 3800 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11918 | 572.1 | M | 2173980
134 | 1500 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11927 | 1175.56 | M | 1763340
135 | 200 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (excluding the cost of Hume Pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11936 | 1319.84 | M | 263968
136 | 1000 | Laying of 33KV XLPE UG cable Single Run of Size in Hard Rock (1.2*0.45x1=0.54cum) | Elect | Labour | SWR11003 | 1287 | M | 1287000
137 | 65 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 178425
138 | 32 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 182424.96
139 | 1000 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 1044000
140 | 400 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 404800
141 | 200 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 25000
142 | 8 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 22118.08
143 | 70 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 9496.2
144 | 6200 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 186000
145 | 65 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 31460
146 | 1.345 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 297.245
147 | 1.345 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 248.825
148 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
149 | 5.845 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2408.6076
150 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
151 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
152 | 18 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 20376
153 | 12 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 11888.16
154 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
155 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
156 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
157 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 74224.278
158 | 0.37 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 1440.41
159 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3340.35
160 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
161 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
162 | 3 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
163 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
164 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
165 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
166 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
167 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | EA | 2640
168 | 6 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
169 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
170 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
171 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
172 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
173 | 7.55 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 5775.75
174 | 26 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 26624
175 | 13 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 42896.1
176 | 26 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 26624
177 | 3550 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11919 | 465.46 | M | 1652383
178 | 3200 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 3436608
179 | 200 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (cxcluding the cost of Hume Pipe)-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11937 | 1199.4 | M | 239880
180 | 600 | Laying of 11KV XLPE UG cable Single Run in Hard Rock (1.05*0.45x1=0.4725cum) | Elect | Labour | SWR11005 | 1075 | M | 645000
181 | 75 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 205875
182 | 28 | Making of 11 KV 3x300 Sqmm Cable Straight through joints | Elect | Labour | SWR10386 | 3725.45 | EA | 104312.6
183 | 1000 | Supply 4" BClass GI pipe 3.65mm thck 12.2Kg/M | Elect | Supply | SMR40080 | 740 | M | 740000
184 | 1000 | Supply 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 759000
185 | 200 | Supply of 4" Hume Pipe | Elect | Supply | SMR40003 | 80 | M | 16000
186 | 16 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
187 | 120 | Raising of Single run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11955 | 144.08 | M | 17289.6
188 | 5400 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 162000
189 | 75 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 36300
190 | 0.614 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 135.694
191 | 0.614 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 113.59
192 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
193 | 4.614 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1901.3371
194 | 16 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
195 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
196 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
197 | 8 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
198 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
199 | 160 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6560
200 | 7.521 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 49480.659
201 | 0.25 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 973.25
202 | 0.23 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Elect | Labour | SWR10869 | 3426 | EA | 787.98
203 | 16 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 44624
204 | 16 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 19747.2
205 | 16 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 6176
206 | 8 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 640
207 | 8 | Un loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 640
208 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
209 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
210 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
211 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
212 | 40 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 4700 |  | 212
Electrical Total Rs. | [7 empty] | 18314745.0111 |  | 95
Civil Portion:
213 | 24 | Clearing of site by hiring JCB, complete for the finished item of work. | Civil | Labour | SWR34179 | 2165 | Hrs | 51960
214 | 2 | Providing contour surveying maps with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5665 | EA | 11330
215 | 2 | Providing report on soil bearing capacity | Civil | Labour | SWR34097 | 4500 | EA | 9000
216 | 7500 | Design and submisiion of 2 sets of structural design drawings with soft copy complete finished item of work | Civil | Labour | SWR33426 | 5 | FT2 | 37500
217 | 27.65 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work including seigniorage excluding dewatering charges etc as per SS - 20 B(APSS 308).Hard rock ( blasting prohibited ). | Civil | Labour | SWR33018 | 1440 | Cum | 39816
218 | 938.7 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work excluding dewatering charges etc as per SS - 20B (APSS 308). Ordinary Soil | Civil | Labour | SWR33015 | 486 | Cum | 456208.2
219 | 108 | Drilling holes in hard granite or sheet rock by Pneumatic compressor 25 mm dia meter etc for complete for item of work | Civil | Labour | SWR34180 | 144 | rmt | 15552
220 | 108 | Grouting the holes with neat cement slurry excluding cost of steel 25 mm dia meter including cost of material labour charges complete fro finished item of work as directed by the engineer in charge | Civil | Labour | SWR34458 | 93 | rmt | 10044
221 | 211.23 | Filling with already available Earthwork in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Civil | Labour | SWR33055 | 202 | Cum | 42668.46
222 | 90.38 | Plain Cement contrete (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4843 | Cum | 437710.34
223 | 82.02 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work. a) Column Footings | Civil | Labour | SWR33098 | 9595 | Cum | 786981.9
224 | 28.46 | RCC M - 20 GF (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. b) Columns" | Civil | Labour | SWR33100 | 13343 | Cum | 379741.78
225 | 4.96 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work c)Plinth Beams | Civil | Labour | SWR33099 | 12465 | Cum | 61826.4
226 | 18.3 | RCC M - 20 GF Beams (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all mater as directed by Engineer incharge of the work. d)Roof Beams" | Civil | Labour | SWR33121 | 12381 | Cum | 226572.3
227 | 1.82 | RCC M - 20 GF Lintels(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Lintels | Civil | Labour | SWR33107 | 13173 | Cum | 23974.86
228 | 43.83 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. / h) Roofslab & Staircase "150mm | Civil | Labour | SWR33128 | 10969 | Cum | 480771.27
229 | 18 | Supplying, fitting and placing HYSD bar reinforcement in foundation complete as per drawings and technical specifications for Bars below 36 mm dia including over laps and wastage, where they are not welded,complete as directed by Engineer incharge of the work. | Civil | Labour | SWR33144 | 75636 | Ton | 1361448
230 | 240.83 | Coursed rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33041 | 5027 | Cum | 1210652.41
231 | 87.84 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | Sqm | 10892.16
232 | 96.26 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 8369 | Cum | 805599.94
233 | 345.87 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification as directed by Engineer incharge of the work. | Civil | Labour | SWR33052 | 493 | Cum | 170513.91
234 | 1628.63 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 559 | Sqm | 910404.17
235 | 265.28 | Providng impervious coat to exposed RCC roof slab surface with CM(1:3), 20 mm thick with 1kg of water proof compound per bag of cement laid over roof when it is green including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33156 | 582 | Sqm | 154392.96
236 | 90 | RCM facia 5cm thick in CM (1:3) for drop walls, fins with rabbit wire mesh & nominal reinforcemet as directed by Engineer-in-change with dubara sponge finishing, including cost & conveyance of all materials to site, seigniorage charges, sales & incidental, cost and conveyance of cement, wire mesh, water to work site, centering, scaffolding and form work, lift changes etc., complete for finished items of work but excluding cost of steel & its fabrication charges, for finished item of work. (APSS No.403 & 903). | Civil | Labour | SWR33203 | 3036 | Sqm | 273240
237 | 22.33 | Supply & fixing Aluminimum Anodised Two/Three Track Sliding Windows as per approved drawing with aluminium anodised sections of Series C Jindal sections and outer frame top horizontals & both verticals of 8774 of size 62 x 29.5 mm and bottom horizontal - two track frame of 8773 of size 62 x 29.5 mm, Shutter frame top, bottom and verticals of 8304 of size 50 mm x 20 mm and Weather interlocking frame of 8306 of size 50 x 20 with plain clear float glass 5mm thick fixed including Supply & fixing aluminium handles of 100 mm for each shutter, nylon rollers assembly and all labour charges for fixing the fixtures with required no. of screws, bolts and nuts and includingt labour charges for fixing the frame in position, fixing shutter to frame etc. completed for finished item of work | Civil | Labour | SWR33277 | 3623 | Sqm | 80901.59
238 | 26.68 | Supply & fixing of ms grill to windows with outer frame of ISA2525 of 25mm thick , horizontal and vertical square rods of 10x10mm and paintng with synthetic enamel paint per (0.3 x 1.2 )sqm. | Civil | Labour | SWR33310 | 2990 | sqm | 79773.2
239 | 7.95 | Supplying & fixing collapsible steel shutters with vertical, double channel of 20 x10x2 mm of 100 mm centre ,Bracers with flat iron 40x40x6 mm with 38 mm dia steel pulleys, the top, bottom and side vertical frames of the collapsible gate with 65x65mmx8mm MS Angle and middle guide rail at site height with 65mmx8mm MS flat for the pulleys to guide and fixed with necessary hold fasts, bolts, nuts, rivets, locking arrangements, stoppers, handles, all accessories all fixtures and painted with one coat of approved steel primer etc., complete for finished item of work as per special spn 1105. | Civil | Labour | SWR33411 | 4017 | Sqm | 31935.15
240 | 3.7 | Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood (Schedule Item No. 301.) complete for finished item of work. | Civil | Labour | SWR33269 | 4371 | Sqm | 16172.7
241 | 9.59 | Flooring with cermic tiles of set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33224 | 913 | Sqm | 8755.67
242 | 225.78 | Flooring with polished shahabad stones 20 mmthick set over base coat of CM (1:3) over already laid CC bed /RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth including cost of all materials like cement, sand, and water and flooring stones etc., complete, including seigniorage charges, labour charges for dresing of flooring stones etc., complete for finished item of work . | Civil | Labour | SWR33219 | 785 | Sqm | 177237.3
243 | 12.5 | Decorated white back ground glazed tiles, set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste mixed with pigment of matching shadeto full depth, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33226 | 882 | Sqm | 11025
244 | 18.22 | Providing skirting to internal walls to 15 cm height/risers of steps with ...mm thick polished Shahabad stone length equal to polished stones, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete, including seigniorage charges, etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33236 | 875 | Sqm | 15942.5
245 | 576.18 | Painting to new walls with 2 coats of ready mixed oil bound wahsable distemper of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 911 for internal walls as directed by Engineer incharge of the work | Civil | Labour | SWR33333 | 146 | Sqm | 84122.28
246 | 1526.94 | Painting to new walls with 2 coats of ACE paint external grade of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 912 for external walls as directed by Engineer incharge of the work. | Civil | Labour | SWR33334 | 154 | Sqm | 235148.76
247 | 9.59 | Supplying and fixing Alluminium glazed door cum fixed window or door using anodised alluminium extruded sections and mat finish for frames sites and Handle/knib,locking arrangements and 4.0mm plain glass fixed to the frame with beeding and qasket with all required item of work. | Civil | Labour | SWR33272 | 6162 | Sqm | 59093.58
248 | 19.68 | Plain Cement contrete (1:2:4) Nominal Mix using 20 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33030 | 6212 | Cum | 122252.16
249 | 30.14 | Plain Cement contrete (1:3:6) Nominal Mix using 40 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33029 | 5133 | Cum | 154708.62
250 | 2354.44 | Supply and fabrication of beams,chanales and angles including labour charges complete for the finished item of work. | Civil | Labour | SWR33145 | 128 | Kg | 301368.32
251 | 333 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | Rmt | 35964
252 | 1 | Supply & fixing 4 way TPN Distribution board with IP-42 protection suitable for 3 phase 40A FP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 12Nos as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
253 | 8 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1328
254 | 2 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 898
255 | 64 | Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 43264
256 | 24 | Supply & Fixing of 28W T5 fluorescent tube. Makes : Crompton / Bajaj / Phillips / Surya / Havells with copper choke,starter etc.,incuding 1No 40W tube etc., complete. | Civil | Labour | SWR33558 | 148 | EA | 3552
257 | 1 | Supply of 12" (300mm)ISI, 900 RPM Light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
258 | 186 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | RMT | 13950
259 | 308 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | RMT | 31724
260 | 16 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 2256
261 | 12 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 27324
262 | 12 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 7068
263 | 10 | Supply & Fixing of 12" heavy duty exhaust fan with metal blades etc including all operational, incidental and labour charges etc. complete for the finished item of worK Makes : Crompton / Havells Ventilair-DB / Orient hill air. | Civil | Labour | SWR33573 | 3887 | EA | 38870
264 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
265 | 10 | S&F 20W LED Tubelight Batten | Civil | Labour | SWR33553 | 582 | EA | 5820
266 | 35 | Supplying, laying, jointing and testing 101.4 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | RMT | 26425
267 | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | Civil | Labour | SWR34296 | 8766 | EA | 8766
268 | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 256
269 | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 200
270 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | RMT | 5544
271 | 5 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | RMT | 2050
272 | 2 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 1534
273 | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap | Civil | Labour | SWR34314 | 2228 | EA | 2228
274 | 1 | Supplying and Fixing best Indian make plastic seat and lid for European water closets with rubber or plastic Buffers as per IS 2548-1996 | Civil | Labour | SWR34315 | 1324 | EA | 1324
275 | 2 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 1442
276 | 4 | S&F 15 mm bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 298 | EA | 1192
277 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
278 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
279 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
280 | 1 | Supplying & Fixing low down Plastic flushing tank 10 Lit Capacity Hindustan Sanitary ware/ parry/ Neycer with internal components | Civil | Labour | SWR34376 | 2032 | EA | 2032
281 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
282 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality complete for finished item of work | Civil | Labour | SWR34426 | 33 | EA | 66
283 | 20 | S & F of (15.90mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | RMT | 4780
284 | 50 | Supply and Fixing of (22.20mm) Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | RMT | 15650
285 | 40 | Supply and Fixing of (28.60mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | RMT | 16400
286 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
287 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 331
288 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
289 | 1 | Supply & fixing NP soap dish heavy type with NP screws | Civil | Labour | SWR34429 | 675 | EA | 675
290 | 17.5 | Supply and fixing of AC sheets including cost of material labour conveyence etc complete for finished item of work as directed by the engineer in charge. | Civil | Labour | SWR33400 | 395 | M2 | 6912.5
291 | 3.05 | S&F of Glow sign board size 10' x 3' including lettering, labour charges, fitting charges cost of all materials and complete for finished item. | Civil | Labour | SWR33422 | 3553 | M2 | 10836.65
292 | 195 | Carting away of excavated soils Complete for finished item of work | Civil | Labour | SWR34151 | 270 | Cum | 52650
293 | 6.27 | Providing 20 mm chips in the transformer area including cost, lead and labour charges complete for finished item of work | Civil | Labour | SWR33057 | 1525 | Cum | 9561.75
294 | 30 | Flooring with chequrred terrazzo tiles of 22 mm thick (medium shade ) set over base coat of cement mortar (1:6) 12 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, complete for finished item of work | Civil | Labour | SWR33222 | 916 | Sqm | 27480
295 | 8.75 | Supply and fixing of MS GATE with redoxide and 2 Coats of Anamil paint Complete finished item of work as directed by Engineer - in-charge | Civil | Labour | SWR33404 | 5299 | sqm | 46366.25
296 | 1 | Geophysical Investgation charges for water point by Geologist as directed by Engineer in chargecomplete for the finished item of work. | Civil | Labour | SWR33608 | 5000 | EA | 5000
297 | 185 | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete 0 to 90M | Civil | Labour | SWR33609 | 336 | Rmt | 62160
298 | 25 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | Rmt | 22075
299 | 1 | Supply and erecting, ISI mark submersible 2.0HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33626 | 21619 | EA | 21619
300 | 168 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cSqm including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | Rmt | 30240
301 | 1 | Supply and erecting D.O.L Starter 250V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33644 | 1040 | EA | 1040
302 | 180 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | Rmt | 34560
303 | 1 | Provd-DGPS & Total Staion Survey | Civil | Labour | SWR34506 | 5000 | EA | 5000
304 | 1 | Providing supply of electricity to the site premises through custamer service centre duly applying for new connection including service wire, application complete the work. | Civil | Labour | SWR33425 | 5408 | EA | 5408
305 | 290 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | Cum | 11600
306 | 558.84 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | Cum | 54486.9
307 | 345.88 | Seigniorage Charges -Gravel | Civil | Labour | SWR34472 | 30 | Cum | 10376.4
| Civil Total in Rs. | [6 empty] | 10099971.34 | 10099971.34
Total (Elect+ Civil ) | [7 empty] | 28414716.3511 | 18314745.03
| GST@18% | [6 empty] | 5114648.9432 | 0.01888
Grand Total (Elect+Civil) incl GST | [7 empty] | 33529365.2943 | 28414716.37
0.01888
33529365.3166
0.022278

## Sulthanshahi
SCHEDULE
Name of the Work :- Erection of 33/11KV Indoor SS with 2Nos 8MVA PTRs Construction of control room, compound wall along with MS gate and borewell, cable trenches, power transformer plinths, toilet block, electrification, sanitary and water supply arrangements for the proposed 33/11 KV Indoor Sub-stationat Sulthanshahi, Charminar in in Bahadurpura Constituency in Operation Hyderabad South Circle in Master Plan, Hyderabad Circle
WBS Element :- S-1766-12-02-02-03-001 & S-1766-12-07-01-02-001(Civil)
Electrical Portion:
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.Number | Rate (INR) | UOM | Amount
1 | 2 | LOADING of 8 MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) - 8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
3 | 2 | UNLOADING of 8 MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
4 | 2 | Erection of 8 MVA PTR | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
5 | 1 | LOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10195 | 350 | EA | 350
6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
7 | 1 | UNLOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10513 | 280 | EA | 280
8 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
9 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc - 3 Phase DTRs 63,75 & 100 KVA | Elect | Labour | SWR20905 | 1650 | EA | 1650
10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space)(excluding of loading unloading) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) (excludingof loading unloading)Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging .Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification | Elect | Supply | SMR40045 | 42000 | EA | 42000
23 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
24 | 8 | LOADING of RSJoists150 x 150 mm/RailPole | Elect | Labour | SWR10205 | 176 | EA | 1408
25 | 8 | UNLOADING of RSJoists150 x150 mm/RailPol | Elect | Labour | SWR10523 | 107 | EA | 856
26 | 0.83 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 183.43
27 | 0.83 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 153.55
28 | 3.83 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1578.2664
29 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
30 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
31 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
32 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
33 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
34 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
35 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 1846.06
36 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
37 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
38 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
39 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
40 | 3.4 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 751.4
41 | 3.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 629
42 | 3.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1401.072
43 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
44 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
45 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
46 | 314 | Paint-Black to all Earth Flat incl. Paint cost | Elect | Labour | SWR12217 | 55 | M | 17270
47 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
48 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
49 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench withearth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
50 | 56 | Raise-33KV 33KV 630sqmm UG Cb on support | Elect | Labour | SWR12448 | 133 | M | 7448
51 | 106 | Lay-33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
52 | 14 | Raising of 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
53 | 8 | S-33KV 1x630Sqmm GIS ID Unit EndTermtn | Elect | Supply | SMR12473 | 2500 | EA | 20000
54 | 8 | S-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Supply | SMR12474 | 4200 | EA | 33600
55 | 8 | Install-33KV 1x630Sqmm GIS ID EndTermtn | Elect | Labour | SWR12473 | 17600 | EA | 140800
56 | 8 | Install-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Labour | SWR12474 | 4000 | EA | 32000
57 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
58 | 85 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
59 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x185 Sqmm Cable | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
60 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
61 | 90 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
62 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
63 | 2 | Supply of 31/2x185Sqmm UG O/D end term kits | Elect | Supply | SMR40140 | 550 | EA | 1100
64 | 2 | Making of Outdoor/Indoor LT 3 1/2 x 185 Sqmm CableCable End Termination | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
65 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 59400
66 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per pecification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
67 | 6 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 456
68 | 1.6 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 659.328
69 | 6 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 300
70 | 1.6 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
71 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
72 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
73 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
74 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
75 | 5 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
76 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
77 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
78 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 603.415
79 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 240
80 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
81 | 1 | Un loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
82 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
83 | 1 | Loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12406 | 80 | EA | 80
84 | 1 | Un loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12425 | 80 | EA | 80
85 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
86 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
87 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
88 | 18 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
89 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elect | Labour | SWR12125 | 14.03 | M | 420.9
90 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
91 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
92 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
93 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 111304
94 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
95 | 8 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
96 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
97 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 965.464
98 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 384
99 | 8 | S-Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
100 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
101 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
102 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
103 | 400 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 33200
104 | 12 | Sup Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
105 | 1 | Sup Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
106 | 2 | Sup TrollyMounted Co2 Cylinders(IS-2878) | Elect | Supply | SMR40087 | 9240 | EA | 18480
107 | 2 | Sup Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elect | Supply | SMR40088 | 1386 | SET | 2772
108 | 6 | Sup Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 27720
109 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
110 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
111 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
112 | 1 | Sup Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
113 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
114 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
115 | 1 | Sup Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
116 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
117 | 1 | SupName board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10238 | EA | 10238
118 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
119 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & keycontaining (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23,24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets,6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) AdjustableSpanner 305 mm length least maximum opening 35mmchrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter,(10) Insulated Cutting Plier Length 8” with cable stripperinsulated with thick C. A. sleeve confirming to IS: 4378 - 1990,(11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm,(13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 4925 | SET | 4925
120 | 1 | Sup Rechargeable LED torch light of Standard make | Elect | Supply | SMR40064 | 1733 | EA | 1733
121 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
122 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
123 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
124 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
125 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
126 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | labour | SWR20032 | 1654 | EA | 1654
127 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | labour | SWR22090 | 2205 | EA | 2205
128 | 1 | S-10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
129 | 8.2 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 6273
130 | 28 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 28672
131 | 15 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 49495.5
132 | 28 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 28672
133 | 5500 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11918 | 572.1 | M | 3146550
134 | 1500 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11927 | 1175.56 | M | 1763340
135 | 200 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (excluding the cost of Hume Pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11936 | 1319.84 | M | 263968
136 | 1000 | Laying of 33KV XLPE UG cable Single Run of Size in Hard Rock (1.2*0.45x1=0.54cum) | Elect | Labour | SWR11003 | 1287 | M | 1287000
137 | 82 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 225090
138 | 28 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 159621.84
139 | 1000 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 1044000
140 | 400 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 404800
141 | 200 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 25000
142 | 8 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 22118.08
143 | 70 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 9496.2
144 | 8200 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 246000
145 | 82 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 39688
146 | 1.345 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 297.245
147 | 1.345 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 248.825
148 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
149 | 5.845 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2408.6076
150 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
151 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
152 | 12 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 13584
153 | 12 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 11888.16
154 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
155 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
156 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
157 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 74224.278
158 | 0.37 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 1440.41
159 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3340.35
160 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
161 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
162 | 3 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
163 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
164 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
165 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
166 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
167 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | EA | 2640
168 | 6 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
169 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
170 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
171 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
172 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
173 | 5.55 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 4245.75
174 | 20 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 20480
175 | 10 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 32997
176 | 20 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 20480
177 | 3550 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11919 | 465.46 | M | 1652383
178 | 1200 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 1288728
179 | 200 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (cxcluding the cost of Hume Pipe)-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11937 | 1199.4 | M | 239880
180 | 600 | Laying of 11KV XLPE UG cable Single Run in Hard Rock (1.05*0.45x1=0.4725cum) | Elect | Labour | SWR11005 | 1075 | M | 645000
181 | 55 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 150975
182 | 20 | Making of 11 KV 3x300 Sqmm Cable Straight through joints | Elect | Labour | SWR10386 | 3725.45 | EA | 74509
183 | 1000 | Supply 4" BClass GI pipe 3.65mm thck 12.2Kg/M | Elect | Supply | SMR40080 | 740 | M | 740000
184 | 1000 | Supply 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 759000
185 | 200 | Supply of 4" Hume Pipe | Elect | Supply | SMR40003 | 80 | M | 16000
186 | 16 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
187 | 120 | Raising of Single run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11955 | 144.08 | M | 17289.6
188 | 5400 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 162000
189 | 55 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 26620
190 | 0.614 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 135.694
191 | 0.614 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 113.59
192 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
193 | 4.614 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1901.3371
194 | 16 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
195 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
196 | 8 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 9056
197 | 8 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
198 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
199 | 160 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6560
200 | 7.521 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 49480.659
201 | 0.25 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 973.25
202 | 0.23 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Elect | Labour | SWR10869 | 3426 | EA | 787.98
203 | 16 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 44624
204 | 16 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 19747.2
205 | 16 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 6176
206 | 8 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 640
207 | 8 | Un loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 640
208 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
209 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
210 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
211 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
212 | 40 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 4700
Electrical Total: | [7 empty] | 17124363.4911
Civil Portion:
213 | 24 | Clearing of site by hiring JCB, complete for the finished item of work. | Civil | Labour | SWR34179 | 2165 | Hrs | 51960
214 | 2 | Providing contour surveying maps with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5665 | EA | 11330
215 | 2 | Providing report on soil bearing capacity | Civil | Labour | SWR34097 | 4500 | EA | 9000
216 | 7500 | Design and submisiion of 2 sets of structural design drawings with soft copy complete finished item of work | Civil | Labour | SWR33426 | 5 | FT2 | 37500
217 | 27.65 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work including seigniorage excluding dewatering charges etc as per SS - 20 B(APSS 308).Hard rock ( blasting prohibited ). | Civil | Labour | SWR33018 | 1440 | Cum | 39816
218 | 938.7 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work excluding dewatering charges etc as per SS - 20B (APSS 308). Ordinary Soil | Civil | Labour | SWR33015 | 486 | Cum | 456208.2
219 | 108 | Drilling holes in hard granite or sheet rock by Pneumatic compressor 25 mm dia meter etc for complete for item of work | Civil | Labour | SWR34180 | 144 | rmt | 15552
220 | 108 | Grouting the holes with neat cement slurry excluding cost of steel 25 mm dia meter including cost of material labour charges complete fro finished item of work as directed by the engineer in charge | Civil | Labour | SWR34458 | 93 | rmt | 10044
221 | 211.23 | Filling with already available Earthwork in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Civil | Labour | SWR33055 | 202 | Cum | 42668.46
222 | 90.38 | Plain Cement contrete (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4843 | Cum | 437710.34
223 | 82.02 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work. a) Column Footings | Civil | Labour | SWR33098 | 9595 | Cum | 786981.9
224 | 28.46 | RCC M - 20 GF (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. b) Columns" | Civil | Labour | SWR33100 | 13343 | Cum | 379741.78
225 | 4.96 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work c)Plinth Beams | Civil | Labour | SWR33099 | 12465 | Cum | 61826.4
226 | 18.3 | RCC M - 20 GF Beams (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all mater as directed by Engineer incharge of the work. d)Roof Beams" | Civil | Labour | SWR33121 | 12381 | Cum | 226572.3
227 | 1.82 | RCC M - 20 GF Lintels(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Lintels | Civil | Labour | SWR33107 | 13173 | Cum | 23974.86
228 | 43.83 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. / h) Roofslab & Staircase "150mm | Civil | Labour | SWR33128 | 10969 | Cum | 480771.27
229 | 18 | Supplying, fitting and placing HYSD bar reinforcement in foundation complete as per drawings and technical specifications for Bars below 36 mm dia including over laps and wastage, where they are not welded,complete as directed by Engineer incharge of the work. | Civil | Labour | SWR33144 | 75636 | Ton | 1361448
230 | 240.83 | Coursed rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33041 | 5027 | Cum | 1210652.41
231 | 87.84 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | Sqm | 10892.16
232 | 96.26 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 8369 | Cum | 805599.94
233 | 345.87 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification as directed by Engineer incharge of the work. | Civil | Labour | SWR33052 | 493 | Cum | 170513.91
234 | 1628.63 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 559 | Sqm | 910404.17
235 | 265.28 | Providng impervious coat to exposed RCC roof slab surface with CM(1:3), 20 mm thick with 1kg of water proof compound per bag of cement laid over roof when it is green including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33156 | 582 | Sqm | 154392.96
236 | 90 | RCM facia 5cm thick in CM (1:3) for drop walls, fins with rabbit wire mesh & nominal reinforcemet as directed by Engineer-in-change with dubara sponge finishing, including cost & conveyance of all materials to site, seigniorage charges, sales & incidental, cost and conveyance of cement, wire mesh, water to work site, centering, scaffolding and form work, lift changes etc., complete for finished items of work but excluding cost of steel & its fabrication charges, for finished item of work. (APSS No.403 & 903). | Civil | Labour | SWR33203 | 3036 | Sqm | 273240
237 | 22.33 | Supply & fixing Aluminimum Anodised Two/Three Track Sliding Windows as per approved drawing with aluminium anodised sections of Series C Jindal sections and outer frame top horizontals & both verticals of 8774 of size 62 x 29.5 mm and bottom horizontal - two track frame of 8773 of size 62 x 29.5 mm, Shutter frame top, bottom and verticals of 8304 of size 50 mm x 20 mm and Weather interlocking frame of 8306 of size 50 x 20 with plain clear float glass 5mm thick fixed including Supply & fixing aluminium handles of 100 mm for each shutter, nylon rollers assembly and all labour charges for fixing the fixtures with required no. of screws, bolts and nuts and includingt labour charges for fixing the frame in position, fixing shutter to frame etc. completed for finished item of work | Civil | Labour | SWR33277 | 3623 | Sqm | 80901.59
238 | 26.68 | Supply & fixing of ms grill to windows with outer frame of ISA2525 of 25mm thick , horizontal and vertical square rods of 10x10mm and paintng with synthetic enamel paint per (0.3 x 1.2 )sqm. | Civil | Labour | SWR33310 | 2990 | sqm | 79773.2
239 | 7.95 | Supplying & fixing collapsible steel shutters with vertical, double channel of 20 x10x2 mm of 100 mm centre ,Bracers with flat iron 40x40x6 mm with 38 mm dia steel pulleys, the top, bottom and side vertical frames of the collapsible gate with 65x65mmx8mm MS Angle and middle guide rail at site height with 65mmx8mm MS flat for the pulleys to guide and fixed with necessary hold fasts, bolts, nuts, rivets, locking arrangements, stoppers, handles, all accessories all fixtures and painted with one coat of approved steel primer etc., complete for finished item of work as per special spn 1105. | Civil | Labour | SWR33411 | 4017 | Sqm | 31935.15
240 | 3.7 | Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood (Schedule Item No. 301.) complete for finished item of work. | Civil | Labour | SWR33269 | 4371 | Sqm | 16172.7
241 | 9.59 | Flooring with cermic tiles of set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33224 | 913 | Sqm | 8755.67
242 | 225.78 | Flooring with polished shahabad stones 20 mmthick set over base coat of CM (1:3) over already laid CC bed /RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth including cost of all materials like cement, sand, and water and flooring stones etc., complete, including seigniorage charges, labour charges for dresing of flooring stones etc., complete for finished item of work . | Civil | Labour | SWR33219 | 785 | Sqm | 177237.3
243 | 12.5 | Decorated white back ground glazed tiles, set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste mixed with pigment of matching shadeto full depth, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33226 | 882 | Sqm | 11025
244 | 18.22 | Providing skirting to internal walls to 15 cm height/risers of steps with ...mm thick polished Shahabad stone length equal to polished stones, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete, including seigniorage charges, etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33236 | 875 | Sqm | 15942.5
245 | 576.18 | Painting to new walls with 2 coats of ready mixed oil bound wahsable distemper of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 911 for internal walls as directed by Engineer incharge of the work | Civil | Labour | SWR33333 | 146 | Sqm | 84122.28
246 | 1526.94 | Painting to new walls with 2 coats of ACE paint external grade of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 912 for external walls as directed by Engineer incharge of the work. | Civil | Labour | SWR33334 | 154 | Sqm | 235148.76
247 | 9.59 | Supplying and fixing Alluminium glazed door cum fixed window or door using anodised alluminium extruded sections and mat finish for frames sites and Handle/knib,locking arrangements and 4.0mm plain glass fixed to the frame with beeding and qasket with all required item of work. | Civil | Labour | SWR33272 | 6162 | Sqm | 59093.58
248 | 19.68 | Plain Cement contrete (1:2:4) Nominal Mix using 20 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33030 | 6212 | Cum | 122252.16
249 | 30.14 | Plain Cement contrete (1:3:6) Nominal Mix using 40 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33029 | 5133 | Cum | 154708.62
250 | 2354.44 | Supply and fabrication of beams,chanales and angles including labour charges complete for the finished item of work. | Civil | Labour | SWR33145 | 128 | Kg | 301368.32
251 | 333 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | Rmt | 35964
252 | 1 | Supply & fixing 4 way TPN Distribution board with IP-42 protection suitable for 3 phase 40A FP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 12Nos as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
253 | 8 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1328
254 | 2 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 898
255 | 64 | Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 43264
256 | 24 | Supply & Fixing of 28W T5 fluorescent tube. Makes : Crompton / Bajaj / Phillips / Surya / Havells with copper choke,starter etc.,incuding 1No 40W tube etc., complete. | Civil | Labour | SWR33558 | 148 | EA | 3552
257 | 1 | Supply of 12" (300mm)ISI, 900 RPM Light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
258 | 186 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | RMT | 13950
259 | 308 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | RMT | 31724
260 | 16 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 2256
261 | 12 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 27324
262 | 12 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 7068
263 | 10 | Supply & Fixing of 12" heavy duty exhaust fan with metal blades etc including all operational, incidental and labour charges etc. complete for the finished item of worK Makes : Crompton / Havells Ventilair-DB / Orient hill air. | Civil | Labour | SWR33573 | 3887 | EA | 38870
264 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
265 | 10 | S&F 20W LED Tubelight Batten | Civil | Labour | SWR33553 | 582 | EA | 5820
266 | 35 | Supplying, laying, jointing and testing 101.4 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | RMT | 26425
267 | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | Civil | Labour | SWR34296 | 8766 | EA | 8766
268 | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 256
269 | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 200
270 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | RMT | 5544
271 | 5 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | RMT | 2050
272 | 2 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 1534
273 | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap | Civil | Labour | SWR34314 | 2228 | EA | 2228
274 | 1 | Supplying and Fixing best Indian make plastic seat and lid for European water closets with rubber or plastic Buffers as per IS 2548-1996 | Civil | Labour | SWR34315 | 1324 | EA | 1324
275 | 2 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 1442
276 | 4 | S&F 15 mm bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 298 | EA | 1192
277 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
278 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
279 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
280 | 1 | Supplying & Fixing low down Plastic flushing tank 10 Lit Capacity Hindustan Sanitary ware/ parry/ Neycer with internal components | Civil | Labour | SWR34376 | 2032 | EA | 2032
281 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
282 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality complete for finished item of work | Civil | Labour | SWR34426 | 33 | EA | 66
283 | 20 | S & F of (15.90mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | RMT | 4780
284 | 50 | Supply and Fixing of (22.20mm) Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | RMT | 15650
285 | 40 | Supply and Fixing of (28.60mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | RMT | 16400
286 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
287 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 331
288 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
289 | 1 | Supply & fixing NP soap dish heavy type with NP screws | Civil | Labour | SWR34429 | 675 | EA | 675
290 | 17.5 | Supply and fixing of AC sheets including cost of material labour conveyence etc complete for finished item of work as directed by the engineer in charge. | Civil | Labour | SWR33400 | 395 | M2 | 6912.5
291 | 3.05 | S&F of Glow sign board size 10' x 3' including lettering, labour charges, fitting charges cost of all materials and complete for finished item. | Civil | Labour | SWR33422 | 3553 | M2 | 10836.65
292 | 195 | Carting away of excavated soils Complete for finished item of work | Civil | Labour | SWR34151 | 270 | Cum | 52650
293 | 6.27 | Providing 20 mm chips in the transformer area including cost, lead and labour charges complete for finished item of work | Civil | Labour | SWR33057 | 1525 | Cum | 9561.75
294 | 30 | Flooring with chequrred terrazzo tiles of 22 mm thick (medium shade ) set over base coat of cement mortar (1:6) 12 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, complete for finished item of work | Civil | Labour | SWR33222 | 916 | Sqm | 27480
295 | 8.75 | Supply and fixing of MS GATE with redoxide and 2 Coats of Anamil paint Complete finished item of work as directed by Engineer - in-charge | Civil | Labour | SWR33404 | 5299 | sqm | 46366.25
296 | 1 | Geophysical Investgation charges for water point by Geologist as directed by Engineer in chargecomplete for the finished item of work. | Civil | Labour | SWR33608 | 5000 | EA | 5000
297 | 185 | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete 0 to 90M | Civil | Labour | SWR33609 | 336 | Rmt | 62160
298 | 25 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | Rmt | 22075
299 | 1 | Supply and erecting, ISI mark submersible 2.0HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33626 | 21619 | EA | 21619
300 | 168 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cSqm including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | Rmt | 30240
301 | 1 | Supply and erecting D.O.L Starter 250V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33644 | 1040 | EA | 1040
302 | 180 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | Rmt | 34560
303 | 1 | Provd-DGPS & Total Staion Survey | Civil | Labour | SWR34506 | 5000 | EA | 5000
304 | 1 | Providing supply of electricity to the site premises through custamer service centre duly applying for new connection including service wire, application complete the work. | Civil | Labour | SWR33425 | 5408 | EA | 5408
305 | 290 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | Cum | 11600
306 | 558.84 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | Cum | 54486.9
307 | 345.88 | Seigniorage Charges -Gravel | Civil | Labour | SWR34472 | 30 | Cum | 10376.4
| Civil Total | [6 empty] | 10099971.34 | 10099971.34
Total (Elect+Civil) | [7 empty] | 27224334.8311 | 17124363.51
18% Service tax on labour: | [7 empty] | 4900380.2696 | 0.01888
Grand Total ( Elect + Civil ) incl GST | [7 empty] | 32124715.1007 | 27224334.85
-0.01888
32124715.123
0.022278

## Shalivahana Nagar
SCHEDULE
Name of the Work :- Erection of 33/11KV Indoor SS with 2Nos 8MVA PTRs Construction of control room, compound wall along with MS gate and borewell, cable trenches, power transformer plinths, toilet block, electrification, sanitary and water supply arrangements for the proposed 33/11 KV Indoor Sub-station at Shalivahana Nagar, Moosarambagh, Malakpet in Bahadurpura Constituency in Operation Hyderabad South Circle in Master Plan Circle, Hyderabad.
WBS Element :- S-1769-12-02-02-03-001 (Elect) & S-1769-12-07-01-02-001 (Civil)
Electrical Portion:
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.Number | Rate (INR) | UOM | Amount
1 | 2 | LOADING of 8 MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) - 8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
3 | 2 | UNLOADING of 8 MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
4 | 2 | Erection of 8 MVA PTR | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
5 | 1 | LOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10195 | 350 | EA | 350
6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
7 | 1 | UNLOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10513 | 280 | EA | 280
8 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
9 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc - 3 Phase DTRs 63,75 & 100 KVA | Elect | Labour | SWR20905 | 1650 | EA | 1650
10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space)(excluding of loading unloading) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) (excludingof loading unloading)Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging .Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification | Elect | Supply | SMR40045 | 42000 | EA | 42000
23 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
24 | 8 | LOADING of RSJoists150 x 150 mm/RailPole | Elect | Labour | SWR10205 | 176 | EA | 1408
25 | 8 | UNLOADING of RSJoists150 x150 mm/RailPol | Elect | Labour | SWR10523 | 107 | EA | 856
26 | 0.83 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 183.43
27 | 0.83 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 153.55
28 | 3.83 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1578.2664
29 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
30 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
31 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
32 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
33 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
34 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
35 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 1846.06
36 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
37 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
38 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
39 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
40 | 3.4 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 751.4
41 | 3.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 629
42 | 3.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1401.072
43 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
44 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
45 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
46 | 314 | Paint-Black to all Earth Flat incl. Paint cost | Elect | Labour | SWR12217 | 55 | M | 17270
47 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
48 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
49 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench withearth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
50 | 56 | Raise-33KV 33KV 630sqmm UG Cb on support | Elect | Labour | SWR12448 | 133 | M | 7448
51 | 106 | Lay-33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
52 | 14 | Raising of 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
53 | 8 | S-33KV 1x630Sqmm GIS ID Unit EndTermtn | Elect | Supply | SMR12473 | 2500 | EA | 20000
54 | 8 | S-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Supply | SMR12474 | 4200 | EA | 33600
55 | 8 | Install-33KV 1x630Sqmm GIS ID EndTermtn | Elect | Labour | SWR12473 | 17600 | EA | 140800
56 | 8 | Install-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Labour | SWR12474 | 4000 | EA | 32000
57 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
58 | 85 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
59 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x185 Sqmm Cable | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
60 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
61 | 90 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
62 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
63 | 2 | Supply of 31/2x185Sqmm UG O/D end term kits | Elect | Supply | SMR40140 | 550 | EA | 1100
64 | 2 | Making of Outdoor/Indoor LT 3 1/2 x 185 Sqmm CableCable End Termination | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
65 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 59400
66 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per pecification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
67 | 6 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 456
68 | 1.6 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 659.328
69 | 6 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 300
70 | 1.6 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
71 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
72 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
73 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
74 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
75 | 5 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
76 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
77 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
78 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 603.415
79 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 240
80 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
81 | 1 | Un loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
82 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
83 | 1 | Loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12406 | 80 | EA | 80
84 | 1 | Un loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12425 | 80 | EA | 80
85 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
86 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
87 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
88 | 18 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
89 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elect | Labour | SWR12125 | 14.03 | M | 420.9
90 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
91 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
92 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
93 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 111304
94 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
95 | 8 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
96 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
97 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3892.98 | M3 | 965.459
98 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 384
99 | 8 | S-Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
100 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
101 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
102 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
103 | 400 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 33200
104 | 12 | Sup Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
105 | 1 | Sup Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
106 | 2 | Sup TrollyMounted Co2 Cylinders(IS-2878) | Elect | Supply | SMR40087 | 9240 | EA | 18480
107 | 2 | Sup Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elect | Supply | SMR40088 | 1386 | SET | 2772
108 | 6 | Sup Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 27720
109 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
110 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
111 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
112 | 1 | Sup Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
113 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
114 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
115 | 1 | Sup Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
116 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
117 | 1 | SupName board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10238 | EA | 10238
118 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
119 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & keycontaining (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23,24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets,6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) AdjustableSpanner 305 mm length least maximum opening 35mmchrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter,(10) Insulated Cutting Plier Length 8” with cable stripperinsulated with thick C. A. sleeve confirming to IS: 4378 - 1990,(11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm,(13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 4925 | SET | 4925
120 | 1 | Sup Rechargeable LED torch light of Standard make | Elect | Supply | SMR40064 | 1733 | EA | 1733
121 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
122 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
123 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
124 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
125 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
126 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | Labour | SWR20032 | 1654 | EA | 1654
127 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | Labour | SWR22090 | 2205 | EA | 2205
128 | 1 | S-10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
129 | 7.5 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 5737.5
130 | 26 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 26624
131 | 13 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 42896.1
132 | 26 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 26624
133 | 3800 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11918 | 572.1 | M | 2173980
134 | 2500 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11927 | 1175.56 | M | 2938900
135 | 200 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (excluding the cost of Hume Pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11936 | 1319.84 | M | 263968
136 | 1000 | Laying of 33KV XLPE UG cable Single Run of Size in Hard Rock (1.2*0.45x1=0.54cum) | Elect | Labour | SWR11003 | 1287 | M | 1287000
137 | 75 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 205875
138 | 28 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 159621.84
139 | 1200 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 1252800
140 | 500 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 506000
141 | 200 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 25000
142 | 8 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 22118.08
143 | 70 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 9496.2
144 | 7500 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 225000
145 | 75 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 36300
146 | 1.345 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 297.245
147 | 1.345 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 248.825
148 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
149 | 5.845 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2408.6076
150 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
151 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
152 | 18 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 20376
153 | 12 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 11888.16
154 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
155 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
156 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
157 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 74224.278
158 | 0.37 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 1440.41
159 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3340.35
160 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
161 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
162 | 3 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
163 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
164 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
165 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
166 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
167 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | EA | 2640
168 | 6 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
169 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
170 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
171 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
172 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
173 | 7.5 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 5737.5
174 | 26 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 26624
175 | 13 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 42896.1
176 | 26 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 26624
177 | 5000 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11919 | 465.46 | M | 2327300
178 | 2000 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 2147880
179 | 200 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (cxcluding the cost of Hume Pipe)-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11937 | 1199.4 | M | 239880
180 | 300 | Laying of 11KV XLPE UG cable Single Run in Hard Rock (1.05*0.45x1=0.4725cum) | Elect | Labour | SWR11005 | 1075 | M | 322500
181 | 75 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 205875
182 | 30 | Making of 11 KV 3x300 Sqmm Cable Straight through joints | Elect | Labour | SWR10386 | 3725.45 | EA | 111763.5
183 | 800 | Supply 4" BClass GI pipe 3.65mm thck 12.2Kg/M | Elect | Supply | SMR40080 | 740 | M | 592000
184 | 300 | Supply 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 227700
185 | 200 | Supply of 4" Hume Pipe | Elect | Supply | SMR40003 | 80 | M | 16000
186 | 16 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
187 | 120 | Raising of Single run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11955 | 144.08 | M | 17289.6
188 | 5500 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 165000
189 | 75 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 36300
190 | 0.614 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 135.694
191 | 0.614 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 113.59
192 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
193 | 4.614 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1901.3371
194 | 16 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
195 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
196 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
197 | 8 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
198 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
199 | 160 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6560
200 | 7.521 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 49480.659
201 | 0.25 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 973.25
202 | 0.23 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Elect | Labour | SWR10869 | 3426 | TO | 787.98
203 | 16 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 44624
204 | 16 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 19747.2
205 | 16 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 6176
206 | 8 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 640
207 | 8 | Un loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 640
208 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
209 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
210 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
211 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
212 | 40 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 4700 | 212
Electrical Total | [7 empty] | 18259149.9362
Civil Portion:
213 | 24 | Clearing of site by hiring JCB, complete for the finished item of work. | Civil | Labour | SWR34179 | 2165 | Hrs | 51960
214 | 2 | Providing contour surveying maps with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5665 | EA | 11330
215 | 2 | Providing report on soil bearing capacity | Civil | Labour | SWR34097 | 4500 | EA | 9000
216 | 7500 | Design and submisiion of 2 sets of structural design drawings with soft copy complete finished item of work | Civil | Labour | SWR33426 | 5 | FT2 | 37500
217 | 13.82 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work including seigniorage excluding dewatering charges etc as per SS - 20 B(APSS 308).Hard rock ( blasting prohibited ). | Civil | Labour | SWR33018 | 1440 | Cum | 19900.8
218 | 647.44 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work excluding dewatering charges etc as per SS - 20B (APSS 308). Ordinary Soil | Civil | Labour | SWR33015 | 486 | Cum | 314655.84
219 | 72 | Drilling holes in hard granite or sheet rock by Pneumatic compressor 25 mm dia meter etc for complete for item of work | Civil | Labour | SWR34180 | 144 | rmt | 10368
220 | 72 | Grouting the holes with neat cement slurry excluding cost of steel 25 mm dia meter including cost of material labour charges complete fro finished item of work as directed by the engineer in charge | Civil | Labour | SWR34458 | 93 | rmt | 6696
221 | 211.23 | Filling with already available Earthwork in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Civil | Labour | SWR33055 | 202 | Cum | 42668.46
222 | 55.83 | Plain Cement contrete (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4843 | Cum | 270384.69
223 | 67.81 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work. a) Column Footings | Civil | Labour | SWR33098 | 9595 | Cum | 650636.95
224 | 23.87 | RCC M - 20 GF (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. b) Columns" | Civil | Labour | SWR33100 | 13343 | Cum | 318497.41
225 | 15.01 | RCC M - 20 FF (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. b) Columns" | Civil | Labour | SWR33101 | 13343 | Cum | 200278.43
226 | 5.22 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work c)Plinth Beams | Civil | Labour | SWR33099 | 12465 | Cum | 65067.3
227 | 13.46 | RCC M - 20 GF Beams (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all mater as directed by Engineer incharge of the work. d)Roof Beams" | Civil | Labour | SWR33121 | 12381 | Cum | 166648.26
228 | 13.46 | RCC M - 20 FF beams(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all mater as directed by Engineer incharge of the work. d)Roof Beams" | Civil | Labour | SWR33122 | 12381 | Cum | 166648.26
229 | 1.82 | RCC M - 20 GF Lintels(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Lintels | Civil | Labour | SWR33107 | 13173 | Cum | 23974.86
230 | 2.34 | RCC M - 20 FF Lintels(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Lintels | Civil | Labour | SWR33108 | 13173 | Cum | 30824.82
231 | 43.83 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. / h) Roofslab & Staircase "150mm | Civil | Labour | SWR33128 | 10969 | Cum | 480771.27
232 | 32.09 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. / h) Roofslab & Staircase "150mm | Civil | Labour | SWR33129 | 10969 | Cum | 351995.21
233 | 17 | Supplying, fitting and placing HYSD bar reinforcement in foundation complete as per drawings and technical specifications for Bars below 36 mm dia including over laps and wastage, where they are not welded,complete as directed by Engineer incharge of the work. | Civil | Labour | SWR33144 | 75636 | Ton | 1285812
234 | 117.62 | Coursed rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33041 | 5027 | Cum | 591275.74
235 | 50.04 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | Sqm | 6204.96
236 | 65.97 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 8369 | Cum | 552102.93
237 | 47.92 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33069 | 8369 | Cum | 401042.48
238 | 318.9 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification as directed by Engineer incharge of the work. | Civil | Labour | SWR33052 | 493 | Cum | 157217.7
239 | 1190.87 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 559 | Sqm | 665696.33
240 | 932.84 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33164 | 559 | Sqm | 521457.56
241 | 212.86 | 2nd floor Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:3), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33165 | 565 | Sqm | 120265.9
242 | 192 | Providng impervious coat to exposed RCC roof slab surface with CM(1:3), 20 mm thick with 1kg of water proof compound per bag of cement laid over roof when it is green including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33156 | 582 | Sqm | 111744
243 | 72.39 | RCM facia 5cm thick in CM (1:3) for drop walls, fins with rabbit wire mesh & nominal reinforcemet as directed by Engineer-in-change with dubara sponge finishing, including cost & conveyance of all materials to site, seigniorage charges, sales & incidental, cost and conveyance of cement, wire mesh, water to work site, centering, scaffolding and form work, lift changes etc., complete for finished items of work but excluding cost of steel & its fabrication charges, for finished item of work. (APSS No.403 & 903). | Civil | Labour | SWR33203 | 3036 | Sqm | 219776.04
244 | 50.4 | Supply & fixing Aluminimum Anodised Two/Three Track Sliding Windows as per approved drawing with aluminium anodised sections of Series C Jindal sections and outer frame top horizontals & both verticals of 8774 of size 62 x 29.5 mm and bottom horizontal - two track frame of 8773 of size 62 x 29.5 mm, Shutter frame top, bottom and verticals of 8304 of size 50 mm x 20 mm and Weather interlocking frame of 8306 of size 50 x 20 with plain clear float glass 5mm thick fixed including Supply & fixing aluminium handles of 100 mm for each shutter, nylon rollers assembly and all labour charges for fixing the fixtures with required no. of screws, bolts and nuts and includingt labour charges for fixing the frame in position, fixing shutter to frame etc. completed for finished item of work | Civil | Labour | SWR33277 | 3623 | Sqm | 182599.2
245 | 62.4 | Supply & fixing of ms grill to windows with outer frame of ISA2525 of 25mm thick , horizontal and vertical square rods of 10x10mm and paintng with synthetic enamel paint per (0.3 x 1.2 )sqm. | Civil | Labour | SWR33310 | 2990 | sqm | 186576
246 | 8.7 | Supplying & fixing collapsible steel shutters with vertical, double channel of 20 x10x2 mm of 100 mm centre ,Bracers with flat iron 40x40x6 mm with 38 mm dia steel pulleys, the top, bottom and side vertical frames of the collapsible gate with 65x65mmx8mm MS Angle and middle guide rail at site height with 65mmx8mm MS flat for the pulleys to guide and fixed with necessary hold fasts, bolts, nuts, rivets, locking arrangements, stoppers, handles, all accessories all fixtures and painted with one coat of approved steel primer etc., complete for finished item of work as per special spn 1105. | Civil | Labour | SWR33411 | 4017 | Sqm | 34947.9
247 | 14.68 | Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood (Schedule Item No. 301.) complete for finished item of work. | Civil | Labour | SWR33269 | 4371 | Sqm | 64166.28
248 | 9.59 | Flooring with cermic tiles of set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33224 | 913 | Sqm | 8755.67
249 | 499 | Flooring with polished shahabad stones 20 mmthick set over base coat of CM (1:3) over already laid CC bed /RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth including cost of all materials like cement, sand, and water and flooring stones etc., complete, including seigniorage charges, labour charges for dresing of flooring stones etc., complete for finished item of work . | Civil | Labour | SWR33219 | 785 | Sqm | 391715
250 | 37.5 | Decorated white back ground glazed tiles, set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste mixed with pigment of matching shadeto full depth, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33226 | 882 | Sqm | 33075
251 | 21.58 | Providing skirting to internal walls to 15 cm height/risers of steps with ...mm thick polished Shahabad stone length equal to polished stones, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete, including seigniorage charges, etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33236 | 723 | Sqm | 15602.34
252 | 582.18 | Painting to new walls with 2 coats of ready mixed oil bound wahsable distemper of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 911 for internal walls as directed by Engineer incharge of the work | Civil | Labour | SWR33333 | 146 | Sqm | 84998.28
253 | 1343.44 | Painting to new walls with 2 coats of ACE paint external grade of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 912 for external walls as directed by Engineer incharge of the work. | Civil | Labour | SWR33334 | 154 | Sqm | 206889.76
254 | 19.18 | Supplying and fixing Alluminium glazed door cum fixed window or door using anodised alluminium extruded sections and mat finish for frames sites and Handle/knib,locking arrangements and 4.0mm plain glass fixed to the frame with beeding and qasket with all required item of work. | Civil | Labour | SWR33272 | 6162 | Sqm | 118187.16
255 | 13.9 | Plain Cement contrete (1:2:4) Nominal Mix using 20 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33030 | 6212 | Cum | 86346.8
256 | 34.64 | Plain Cement contrete (1:3:6) Nominal Mix using 40 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33029 | 5133 | Cum | 177807.12
257 | 2442.25 | Supply and fabrication of beams,chanales and angles including labour charges complete for the finished item of work. | Civil | Labour | SWR33145 | 128 | Kg | 312608
258 | 470.5 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | Rmt | 50814
259 | 2 | Supply & fixing 4 way TPN Distribution board with IP-42 protection suitable for 3 phase 40A FP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 12Nos as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 22706
260 | 6 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 996
261 | 4 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 1796
262 | 56 | Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 37856
263 | 24 | Supply & Fixing of 28W T5 fluorescent tube. Makes : Crompton / Bajaj / Phillips / Surya / Havells with copper choke,starter etc.,incuding 1No 40W tube etc., complete. | Civil | Labour | SWR33558 | 148 | EA | 3552
264 | 1 | Supply of 12" (300mm)ISI, 900 RPM Light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
265 | 270 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | RMT | 20250
266 | 340 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | RMT | 35020
267 | 16 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 2256
268 | 8 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 18216
269 | 8 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 4712
270 | 8 | Supply & Fixing of 12" heavy duty exhaust fan with metal blades etc including all operational, incidental and labour charges etc. complete for the finished item of worK Makes : Crompton / Havells Ventilair-DB / Orient hill air. | Civil | Labour | SWR33573 | 3887 | EA | 31096
271 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
272 | 10 | S&F 20W LED Tubelight Batten | Civil | Labour | SWR33553 | 582 | EA | 5820
273 | 50 | Supplying, laying, jointing and testing 101.4 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | RMT | 37750
274 | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | Civil | Labour | SWR34296 | 8766 | EA | 8766
275 | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 256
276 | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 200
277 | 10 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | RMT | 4620
278 | 5 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | RMT | 2050
279 | 2 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 1534
280 | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap | Civil | Labour | SWR34314 | 2228 | EA | 2228
281 | 1 | Supplying and Fixing best Indian make plastic seat and lid for European water closets with rubber or plastic Buffers as per IS 2548-1996 | Civil | Labour | SWR34315 | 1324 | EA | 1324
282 | 2 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 1442
283 | 4 | S&F 15 mm bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 298 | EA | 1192
284 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
285 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
286 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
287 | 1 | Supplying & Fixing low down Plastic flushing tank 10 Lit Capacity Hindustan Sanitary ware/ parry/ Neycer with internal components | Civil | Labour | SWR34376 | 2032 | EA | 2032
288 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
289 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality complete for finished item of work | Civil | Labour | SWR34426 | 33 | EA | 66
290 | 25 | S & F of (15.90mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | RMT | 5975
291 | 50 | Supply and Fixing of (22.20mm) Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | RMT | 15650
292 | 40 | Supply and Fixing of (28.60mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | RMT | 16400
293 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
294 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 331
295 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
296 | 1 | Supply & fixing NP soap dish heavy type with NP screws | Civil | Labour | SWR34429 | 675 | EA | 675
297 | 17.5 | Supply and fixing of AC sheets including cost of material labour conveyence etc complete for finished item of work as directed by the engineer in charge. | Civil | Labour | SWR33400 | 395 | M2 | 6912.5
298 | 3.05 | S&F of Glow sign board size 10' x 3' including lettering, labour charges, fitting charges cost of all materials and complete for finished item. | Civil | Labour | SWR33422 | 3553 | Sqm | 10836.65
299 | 167.56 | Carting away of excavated soils Complete for finished item of work | Civil | Labour | SWR34151 | 270 | Cum | 45241.2
300 | 7.45 | Providing 20 mm chips in the transformer area including cost, lead and labour charges complete for finished item of work | Civil | Labour | SWR33057 | 1525 | Cum | 11361.25
301 | 20.86 | Supply and fixing of MS GATE with redoxide and 2 Coats of Anamil paint Complete finished item of work as directed by Engineer - in-charge | Civil | Labour | SWR33404 | 5299 | sqm | 110537.14
302 | 1 | Geophysical Investgation charges for water point by Geologist as directed by Engineer in chargecomplete for the finished item of work. | Civil | Labour | SWR33608 | 5000 | Sqm | 5000
303 | 155 | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete 0 to 90M | Civil | Labour | SWR33609 | 336 | Rmt | 52080
304 | 25 | Supply and fixing of 180mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | Rmt | 22075
305 | 1 | Supply and erecting, ISI mark submersible 2.0HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33626 | 21619 | EA | 21619
306 | 120 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cSqm including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | Rmt | 21600
307 | 1 | Supply and erecting D.O.L Starter 250V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33644 | 1040 | EA | 1040
308 | 180 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | Rmt | 34560
309 | 1 | Provd-DGPS & Total Staion Survey | Civil | Labour | SWR34506 | 5000 | EA | 5000
310 | 1 | Providing supply of electricity to the site premises through custamer service centre duly applying for new connection including service wire, application complete the work. | Civil | Labour | SWR33425 | 5408 | EA | 5408
311 | 366.2896 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | Cum | 14651.584
312 | 706.9 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | Cum | 68922.75
313 | 320 | Seigniorage Charges -Gravel | Civil | Labour | SWR34472 | 30 | Cum | 9600
Civil Total | [7 empty] | 10571797.784 | 10571797.8
| Total ( Elect + Civil) | [6 empty] | 28830947.7202 | 0.016
18 % GST | [7 empty] | 5189570.5896 | 18259149.96
Grand Total ( Elect + Civil) incl GST | [7 empty] | 34020518.3098 | 0.02384
28830947.76
0.03984
34020518.3568
0.047011

## RTC Bus Depo,DSNR
SCHEDULE
Name of the Work :- Erection of 33/11KV Indoor SS with 2Nos 8MVA PTRs along with Construction of control room, compound wall along with MS gate and bore well, cable trenches, power transformer plinths, toilet block, electrification, sanitary and water supply arrangements for the proposed 33/11 KV Indoor Sub station at RTC Bus Depo, Dilshukhnagar in Malakpet Constituency in Operation Hyderabad South Circle in Master Plan, Hyderabad Circle.
WBS Element :- S-1770-12-02-02-03-001 ( Elect) & S-1770-12-07-01-02-001(Civil)
Electrical Portion:
Sl No | Estimate Qty | Description of item | Work Type | Item Short Description | APSS / Month Cl.Number | Rate (INR) | UOM | Amount
1 | 2 | LOADING of 8 MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) - 8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
3 | 2 | UNLOADING of 8 MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
4 | 2 | Erection of 8 MVA PTR | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
5 | 1 | LOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10195 | 350 | EA | 350
6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
7 | 1 | UNLOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10513 | 280 | EA | 280
8 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
9 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc - 3 Phase DTRs 63,75 & 100 KVA | Elect | Labour | SWR20905 | 1650 | EA | 1650
10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space)(excluding of loading unloading) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) (excludingof loading unloading)Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging .Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification | Elect | Supply | SMR40045 | 42000 | EA | 42000
23 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
24 | 8 | LOADING of RSJoists150 x 150 mm/RailPole | Elect | Labour | SWR10205 | 176 | EA | 1408
25 | 8 | UNLOADING of RSJoists150 x150 mm/RailPol | Elect | Labour | SWR10523 | 107 | EA | 856
26 | 0.83 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 183.43
27 | 0.83 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 153.55
28 | 3.83 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1578.2664
29 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
30 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
31 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
32 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
33 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
34 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
35 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 1846.06
36 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
37 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
38 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
39 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
40 | 3.4 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 751.4
41 | 3.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 629
42 | 3.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1401.072
43 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
44 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
45 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
46 | 314 | Paint-Black to all Earth Flat incl. Paint cost | Elect | Labour | SWR12217 | 55 | M | 17270
47 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
48 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
49 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench withearth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
50 | 56 | Raise-33KV 33KV 630sqmm UG Cb on support-Single Circuit | Elect | Labour | SWR12448 | 133 | M | 7448
51 | 106 | Laying -Second 33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
52 | 14 | Raising of 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
53 | 8 | S-33KV 1x630Sqmm GIS ID Unit EndTermtn | Elect | Supply | SMR12473 | 2500 | EA | 20000
54 | 8 | S-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Supply | SMR12474 | 4200 | EA | 33600
55 | 8 | Install-33KV 1x630Sqmm GIS ID EndTermtn | Elect | Labour | SWR12473 | 17600 | EA | 140800
56 | 8 | Install-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Labour | SWR12474 | 4000 | EA | 32000
57 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
58 | 85 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
59 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x185 Sqmm Cable-Single Run | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
60 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
61 | 90 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
62 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - LT 3 1/2 x 185 Sqmm Cable-Single Run | Elect | Labour | SWR11959 | 85.43 | M | 854.3
63 | 2 | Supply of 31/2x185Sqmm UG O/D end term kits | Elect | Supply | SMR40140 | 550 | EA | 1100
64 | 2 | Making of Outdoor/Indoor LT 3 1/2 x 185 Sqmm CableCable End Termination | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
65 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 59400
66 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per pecification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
67 | 6 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 456
68 | 1.6 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 659.328
69 | 6 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 300
70 | 1.6 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
71 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
72 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
73 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
74 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
75 | 5 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
76 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
77 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
78 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 603.415
79 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 240
80 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
81 | 1 | Un loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
82 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
83 | 1 | Loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12406 | 80 | EA | 80
84 | 1 | Un loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12425 | 80 | EA | 80
85 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
86 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
87 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
88 | 18 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
89 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elect | Labour | SWR12125 | 14.03 | M | 420.9
90 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
91 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
92 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
93 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 111304
94 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
95 | 8 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
96 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
97 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3892.98 | M3 | 965.459
98 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 384
99 | 8 | S-Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
100 | 50 | Supply of GI Bolts & Nuts etc. | Elect | Supply | SMR11488 | 117.5 | KG | 5875
101 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
102 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
103 | 400 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 33200
104 | 12 | Sup Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
105 | 1 | Sup Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
106 | 2 | Sup TrollyMounted Co2 Cylinders(IS-2878) | Elect | Supply | SMR40087 | 9240 | EA | 18480
107 | 2 | Sup Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elect | Supply | SMR40088 | 1386 | SET | 2772
108 | 6 | Sup Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 27720
109 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
110 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
111 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
112 | 1 | Sup Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
113 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
114 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
115 | 1 | Sup Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
116 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
117 | 1 | SupName board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10238 | EA | 10238
118 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
119 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & keycontaining (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23,24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets,6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) AdjustableSpanner 305 mm length least maximum opening 35mmchrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter,(10) Insulated Cutting Plier Length 8” with cable stripperinsulated with thick C. A. sleeve confirming to IS: 4378 - 1990,(11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm,(13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 4925 | SET | 4925
120 | 1 | Sup Rechargeable LED torch light of Standard make | Elect | Supply | SMR40064 | 1733 | EA | 1733
121 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
122 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
123 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
124 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
125 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
126 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | labour | SWR20032 | 1654 | EA | 1654
127 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | labour | SWR22090 | 2205 | EA | 2205
128 | 1 | S-10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
129 | 8 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 6120
130 | 27 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 27648
131 | 14 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 46195.8
132 | 27 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 27648
133 | 3500 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11918 | 572.1 | M | 2002350
134 | 2300 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11927 | 1175.56 | M | 2703788
135 | 200 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (excluding the cost of Hume Pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11936 | 1319.84 | M | 263968
136 | 2000 | Laying of 33KV XLPE UG cable Single Run of Size in Hard Rock (1.2*0.45x1=0.54cum) | Elect | Labour | SWR11003 | 1287 | RMT | 2574000
137 | 80 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 219600
138 | 28 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 159621.84
139 | 1000 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 1044000
140 | 200 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 202400
141 | 200 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 25000
142 | 8 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 22118.08
143 | 70 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 9496.2
144 | 6500 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 195000
145 | 80 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 38720
146 | 1.345 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 297.245
147 | 1.345 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 248.825
148 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
149 | 5.845 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2408.6076
150 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
151 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
152 | 18 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 20376
153 | 12 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 11888.16
154 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
155 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
156 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
157 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 74224.278
158 | 0.37 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 1440.41
159 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3340.35
160 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
161 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
162 | 3 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
163 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
164 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
165 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
166 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
167 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | EA | 2640
168 | 6 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
169 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
170 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
171 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
172 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
173 | 5.5 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 4207.5
174 | 19 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 19456
175 | 10 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 32997
176 | 19 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 19456
177 | 2000 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road | Elect | Labour | SWR11919 | 465.46 | M | 930920
178 | 3000 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 3221820
179 | 200 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (cxcluding the cost of Hume Pipe)-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11937 | 1199.4 | M | 239880
180 | 300 | Laying of 11KV XLPE UG cable Single Run in Hard Rock (1.05*0.45x1=0.4725cum) | Elect | Labour | SWR11005 | 1075 | RMT | 322500
181 | 55 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 150975
182 | 20 | Making of 11 KV 3x300 Sqmm Cable Straight through joints | Elect | Labour | SWR10386 | 3725.45 | EA | 74509
183 | 800 | Supply 4" BClass GI pipe 3.65mm thck 12.2Kg/M | Elect | Supply | SMR40080 | 740 | M | 592000
184 | 300 | Supply 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 227700
185 | 200 | Supply of 4" Hume Pipe | Elect | Supply | SMR40003 | 80 | M | 16000
186 | 16 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
187 | 120 | Raising of Single run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11955 | 144.08 | M | 17289.6
188 | 5000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 150000
189 | 55 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 26620
190 | 0.614 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 220.99 | TO | 135.6879
191 | 0.614 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 113.59
192 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
193 | 4.614 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1901.3371
194 | 16 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
195 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
196 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
197 | 8 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
198 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
199 | 160 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6560
200 | 7.521 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 49480.659
201 | 0.25 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 973.25
202 | 0.23 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Elect | Labour | SWR10869 | 3426 | TO | 787.98
203 | 16 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 44624
204 | 16 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 19747.2
205 | 16 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 6176
206 | 8 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 640
207 | 8 | Un loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 640
208 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
209 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
210 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
211 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
212 | 40 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 4700
| Electrical in Rs. | [6 empty] | 18153843.53
Civil Portion
213 | 24 | Clearing of site by hiring JCB, complete for the finished item of work. | Civil | Labour | SWR34179 | 2165 | Hrs | 51960
214 | 2 | Providing contour surveying maps with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5665 | EA | 11330
215 | 2 | Providing report on soil bearing capacity | Civil | Labour | SWR34097 | 4500 | EA | 9000
216 | 7500 | Design and submisiion of 2 sets of structural design drawings with soft copy complete finished item of work | Civil | Labour | SWR33426 | 5 | FT2 | 37500
217 | 20.74 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work including seigniorage excluding dewatering charges etc as per SS - 20 B(APSS 308).Hard rock ( blasting prohibited ). | Civil | Labour | SWR33018 | 1440 | Cum | 29865.6
218 | 947 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work excluding dewatering charges etc as per SS - 20B (APSS 308). Ordinary Soil | Civil | Labour | SWR33015 | 486 | Cum | 460242
219 | 108 | Drilling holes in hard granite or sheet rock by Pneumatic compressor 25 mm dia meter etc for complete for item of work | Civil | Labour | SWR34180 | 144 | m | 15552
220 | 108 | Grouting the holes with neat cement slurry excluding cost of steel 25 mm dia meter including cost of material labour charges complete fro finished item of work as directed by the engineer in charge | Civil | Labour | SWR34458 | 93 | EA | 10044
221 | 211.23 | Filling with already available Earthwork in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Civil | Labour | SWR33055 | 202 | Cum | 42668.46
222 | 90.38 | Plain Cement contrete (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4843 | Cum | 437710.34
223 | 82.02 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work. a) Column Footings | Civil | Labour | SWR33098 | 9595 | Cum | 786981.9
224 | 28.46 | RCC M - 20 GF (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. b) Columns" | Civil | Labour | SWR33100 | 13343 | Cum | 379741.78
225 | 4.96 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work c)Plinth Beams | Civil | Labour | SWR33099 | 12465 | Cum | 61826.4
226 | 18.3 | RCC M - 20 GF Beams (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all mater as directed by Engineer incharge of the work. d)Roof Beams" | Civil | Labour | SWR33121 | 12381 | Cum | 226572.3
227 | 1.82 | RCC M - 20 GF Lintels(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Lintels | Civil | Labour | SWR33107 | 13173 | Cum | 23974.86
228 | 43.83 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. / h) Roofslab & Staircase "150mm-Ground Floor | Civil | Labour | SWR33128 | 10969 | Cum | 480771.27
229 | 18 | Supplying, fitting and placing HYSD bar reinforcement in foundation complete as per drawings and technical specifications for Bars below 36 mm dia including over laps and wastage, where they are not welded,complete as directed by Engineer incharge of the work. | Civil | Labour | SWR33144 | 75636 | Ton | 1361448
230 | 244 | Coursed rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33041 | 5027 | Cum | 1226588
231 | 87.84 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | Sqm | 10892.16
232 | 99.34 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 8369 | Cum | 831376.46
233 | 345.87 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification as directed by Engineer incharge of the work. | Civil | Labour | SWR33052 | 493 | Cum | 170513.91
234 | 1671.86 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 559 | Sqm | 934569.74
235 | 265.28 | Providng impervious coat to exposed RCC roof slab surface with CM(1:3), 20 mm thick with 1kg of water proof compound per bag of cement laid over roof when it is green including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33156 | 582 | Sqm | 154392.96
236 | 90 | RCM facia 5cm thick in CM (1:3) for drop walls, fins with rabbit wire mesh & nominal reinforcemet as directed by Engineer-in-change with dubara sponge finishing, including cost & conveyance of all materials to site, seigniorage charges, sales & incidental, cost and conveyance of cement, wire mesh, water to work site, centering, scaffolding and form work, lift changes etc., complete for finished items of work but excluding cost of steel & its fabrication charges, for finished item of work. (APSS No.403 & 903). | Civil | Labour | SWR33203 | 3036 | Sqm | 273240
237 | 22.33 | Supply & fixing Aluminimum Anodised Two/Three Track Sliding Windows as per approved drawing with aluminium anodised sections of Series C Jindal sections and outer frame top horizontals & both verticals of 8774 of size 62 x 29.5 mm and bottom horizontal - two track frame of 8773 of size 62 x 29.5 mm, Shutter frame top, bottom and verticals of 8304 of size 50 mm x 20 mm and Weather interlocking frame of 8306 of size 50 x 20 with plain clear float glass 5mm thick fixed including Supply & fixing aluminium handles of 100 mm for each shutter, nylon rollers assembly and all labour charges for fixing the fixtures with required no. of screws, bolts and nuts and includingt labour charges for fixing the frame in position, fixing shutter to frame etc. completed for finished item of work | Civil | Labour | SWR33277 | 3623 | Sqm | 80901.59
238 | 26.68 | Supply & fixing of ms grill to windows with outer frame of ISA2525 of 25mm thick , horizontal and vertical square rods of 10x10mm and paintng with synthetic enamel paint per (0.3 x 1.2 )sqm. | Civil | Labour | SWR33310 | 2990 | sqm | 79773.2
239 | 7.95 | Supplying & fixing collapsible steel shutters with vertical, double channel of 20 x10x2 mm of 100 mm centre ,Bracers with flat iron 40x40x6 mm with 38 mm dia steel pulleys, the top, bottom and side vertical frames of the collapsible gate with 65x65mmx8mm MS Angle and middle guide rail at site height with 65mmx8mm MS flat for the pulleys to guide and fixed with necessary hold fasts, bolts, nuts, rivets, locking arrangements, stoppers, handles, all accessories all fixtures and painted with one coat of approved steel primer etc., complete for finished item of work as per special spn 1105. | Civil | Labour | SWR33411 | 4017 | Sqm | 31935.15
240 | 3.7 | Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood (Schedule Item No. 301.) complete for finished item of work. | Civil | Labour | SWR33269 | 4371 | Sqm | 16172.7
241 | 9.59 | Flooring with cermic tiles of set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33224 | 913 | Sqm | 8755.67
242 | 225.78 | Flooring with polished shahabad stones 20 mmthick set over base coat of CM (1:3) over already laid CC bed /RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth including cost of all materials like cement, sand, and water and flooring stones etc., complete, including seigniorage charges, labour charges for dresing of flooring stones etc., complete for finished item of work . | Civil | Labour | SWR33219 | 785 | Sqm | 177237.3
243 | 12.5 | Decorated white back ground glazed tiles, set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste mixed with pigment of matching shadeto full depth, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33226 | 882 | Sqm | 11025
244 | 18.22 | Providing skirting to internal walls to 15 cm height/risers of steps with ...mm thick polished Shahabad stone length equal to polished stones, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete, including seigniorage charges, etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33236 | 875 | Sqm | 15942.5
245 | 576.18 | Painting to new walls with 2 coats of ready mixed oil bound wahsable distemper of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 911 for internal walls as directed by Engineer incharge of the work | Civil | Labour | SWR33333 | 146 | Sqm | 84122.28
246 | 1526.94 | Painting to new walls with 2 coats of ACE paint external grade of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 912 for external walls as directed by Engineer incharge of the work. | Civil | Labour | SWR33334 | 154 | Sqm | 235148.76
247 | 9.59 | Supplying and fixing Alluminium glazed door cum fixed window or door using anodised alluminium extruded sections and mat finish for frames sites and Handle/knib,locking arrangements and 4.0mm plain glass fixed to the frame with beeding and qasket with all required item of work. | Civil | Labour | SWR33272 | 6162 | Sqm | 59093.58
248 | 21.3 | Plain Cement contrete (1:2:4) Nominal Mix using 20 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33030 | 6212 | Cum | 132315.6
249 | 30.14 | Plain Cement contrete (1:3:6) Nominal Mix using 40 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33029 | 5133 | Cum | 154708.62
250 | 2354.4 | Supply and fabrication of beams,chanales and angles including labour charges complete for the finished item of work. | Civil | Labour | SWR33145 | 128 | Kg | 301363.2
251 | 337 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | Rmt | 36396
252 | 1 | Supply & fixing 4 way TPN Distribution board with IP-42 protection suitable for 3 phase 40A FP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 12Nos as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
253 | 8 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1328
254 | 2 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 898
255 | 64 | Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 43264
256 | 24 | Supply & Fixing of 28W T5 fluorescent tube. Makes : Crompton / Bajaj / Phillips / Surya / Havells with copper choke,starter etc.,incuding 1No 40W tube etc., complete. | Civil | Labour | SWR33558 | 148 | EA | 3552
257 | 1 | Supply of 12" (300mm)ISI, 900 RPM Light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
258 | 186 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | RMT | 13950
259 | 308 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | RMT | 31724
260 | 16 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 2256
261 | 12 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 27324
262 | 12 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 7068
263 | 10 | Supply & Fixing of 12" heavy duty exhaust fan with metal blades etc including all operational, incidental and labour charges etc. complete for the finished item of worK Makes : Crompton / Havells Ventilair-DB / Orient hill air. | Civil | Labour | SWR33573 | 3887 | EA | 38870
264 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
265 | 10 | S&F 20W LED Tubelight Batten | Civil | Labour | SWR33553 | 582 | EA | 5820
266 | 35 | Supplying, laying, jointing and testing 101.4 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | RMT | 26425
267 | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | Civil | Labour | SWR34296 | 8766 | EA | 8766
268 | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 256
269 | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 200
270 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | RMT | 5544
271 | 5 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | RMT | 2050
272 | 2 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 1534
273 | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap | Civil | Labour | SWR34314 | 2228 | EA | 2228
274 | 1 | Supplying and Fixing best Indian make plastic seat and lid for European water closets with rubber or plastic Buffers as per IS 2548-1996 | Civil | Labour | SWR34315 | 1324 | EA | 1324
275 | 2 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 1442
276 | 4 | S&F 15 mm bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 298 | EA | 1192
277 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
278 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
279 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
280 | 1 | Supplying & Fixing low down Plastic flushing tank 10 Lit Capacity Hindustan Sanitary ware/ parry/ Neycer with internal components | Civil | Labour | SWR34376 | 2032 | EA | 2032
281 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
282 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality complete for finished item of work | Civil | Labour | SWR34426 | 33 | EA | 66
283 | 20 | S & F of (15.90mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | RMT | 4780
284 | 50 | Supply and Fixing of (22.20mm) Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | RMT | 15650
285 | 40 | Supply and Fixing of (28.60mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | RMT | 16400
286 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
287 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 331
288 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
289 | 1 | Supply & fixing NP soap dish heavy type with NP screws | Civil | Labour | SWR34429 | 675 | EA | 675
290 | 17.5 | Supply and fixing of AC sheets including cost of material labour conveyence etc complete for finished item of work as directed by the engineer in charge. | Civil | Labour | SWR33400 | 395 | Sqm | 6912.5
291 | 3.05 | S&F of Glow sign board size 10' x 3' including lettering, labour charges, fitting charges cost of all materials and complete for finished item. | Civil | Labour | SWR33422 | 3553 | Sqm | 10836.65
292 | 195.02 | Carting away of excavated soils Complete for finished item of work | Civil | Labour | SWR34151 | 270 | Cum | 52655.4
293 | 6.27 | Providing 20 mm chips in the transformer area including cost, lead and labour charges complete for finished item of work | Civil | Labour | SWR33057 | 1525 | Cum | 9561.75
294 | 20.88 | Supply and fixing of MS GATE with redoxide and 2 Coats of Anamil paint Complete finished item of work as directed by Engineer - in-charge | Civil | Labour | SWR33404 | 5299 | Sqm | 110643.12
295 | 1 | Geophysical Investgation charges for water point by Geologist as directed by Engineer in chargecomplete for the finished item of work. | Civil | Labour | SWR33608 | 5000 | EA | 5000
296 | 185 | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete 0 to 90M | Civil | Labour | SWR33609 | 336 | M | 62160
297 | 25 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | Rmt | 22075
298 | 1 | Supply and erecting, ISI mark submersible 2.0HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33626 | 21619 | EA | 21619
299 | 168 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cSqm including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 30240
300 | 1 | Supply and erecting D.O.L Starter 250V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33644 | 1040 | EA | 1040
301 | 180 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 34560
302 | 1 | Provd-DGPS & Total Staion Survey | Civil | Labour | SWR34506 | 5000 | EA | 5000
303 | 1 | Providing supply of electricity to the site premises through custamer service centre duly applying for new connection including service wire, application complete the work. | Civil | Labour | SWR33425 | 5408 | EA | 5408
304 | 293.24 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | Cum | 11729.6
305 | 563.87 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | Cum | 54977.325
306 | 300 | Seigniorage Charges -Gravel | Civil | Labour | SWR34472 | 30 | Cum | 9000
Civil Total | [7 empty] | 10206468.635 | 10206468.64
Total (Elect + Civil) | [7 empty] | 28360312.165 | 18153843.59
GST @ 18 % | [7 empty] | 5104856.1897 | 28360312.23 | 0.05998
Grand Total ( Elect + Civil) incl GST | [7 empty] | 33465168.3547 | 0.06498
33465168.4314
0.076676

## GHMC Play Ground,Yakathpura
SCHEDULE
Name of the Work :- Erection of 33/11KV Indoor SS with 2Nos 8MVA PTRs along with Construction of control room, compound wall along with MS gate and bore well, cable trenches, power transformer plinths, toilet block, electrification, sanitary and water supply arrangements for the proposed 33/11 KV Indoor Sub station at GHMC Play Ground, Somnadh Nagar,Yakathpura in Bahadurpura Constituency in Operation Hyderabad South Circle in Master Plan , Hyderabad Circle.
WBS Element :- S-1771-12-02-02-03-001 ( Elect) & S-1771-12-07-01-02-001 ( Civil)
Electrical Portion:
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.Number | Rate (INR) | UOM | AMOUNT
1 | 2 | LOADING of 8 MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) - 8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
3 | 2 | UNLOADING of 8 MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
4 | 2 | Erection of 8 MVA PTR | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
5 | 1 | LOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10195 | 350 | EA | 350
6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
7 | 1 | UNLOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10513 | 280 | EA | 280
8 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
9 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc - 3 Phase DTRs 63,75 & 100 KVA | Elect | Labour | SWR20905 | 1650 | EA | 1650
10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space)(excluding of loading unloading) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) (excludingof loading unloading)Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging .Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification | Elect | Labour | SMR40045 | 42000 | EA | 42000
23 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
24 | 8 | LOADING of RSJoists150 x 150 mm/RailPole | Elect | Labour | SWR10205 | 176 | EA | 1408
25 | 8 | UNLOADING of RSJoists150 x150 mm/RailPol | Elect | Labour | SWR10523 | 107 | EA | 856
26 | 0.83 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 183.43
27 | 0.83 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 153.55
28 | 3.83 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1578.2664
29 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
30 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
31 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
32 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
33 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
34 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
35 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 1846.06
36 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
37 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
38 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
39 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
40 | 3.4 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 751.4
41 | 3.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 629
42 | 3.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1401.072
43 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
44 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
45 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
46 | 314 | Paint-Black to all Earth Flat incl. Paint cost | Elect | Labour | SWR12217 | 55 | M | 17270
47 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
48 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
49 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench withearth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
50 | 56 | Raise-33KV 33KV 630sqmm UG Cb on support | Elect | Labour | SWR12448 | 133 | M | 7448
51 | 106 | Lay-33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
52 | 14 | Raising of 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
53 | 8 | S-33KV 1x630Sqmm GIS ID Unit EndTermtn | Elect | Supply | SMR12473 | 2500 | EA | 20000
54 | 8 | S-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Supply | SMR12474 | 4200 | EA | 33600
55 | 8 | Install-33KV 1x630Sqmm GIS ID EndTermtn | Elect | Labour | SWR12473 | 17600 | EA | 140800
56 | 8 | Install-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Labour | SWR12474 | 4000 | EA | 32000
57 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
58 | 85 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road - 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
59 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x185 Sqmm Cable | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
60 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
61 | 90 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
62 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
63 | 2 | Supply of 31/2x185Sqmm UG O/D end term kits | Elect | Supply | SMR40140 | 550 | EA | 1100
64 | 2 | Making of Outdoor/Indoor LT 3 1/2 x 185 Sqmm CableCable End Termination | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
65 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 59400
66 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per pecification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
67 | 6 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 456
68 | 1.6 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 659.328
69 | 6 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 300
70 | 1.6 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
71 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
72 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
73 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
74 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
75 | 5 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
76 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
77 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
78 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 603.415
79 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 240
80 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
81 | 1 | Un loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
82 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
83 | 1 | Loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12406 | 80 | EA | 80
84 | 1 | Un loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12425 | 80 | EA | 80
85 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
86 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
87 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
88 | 18 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
89 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elect | Labour | SWR12125 | 14.03 | M | 420.9
90 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
91 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
92 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
93 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 111304
94 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
95 | 8 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
96 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
97 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 965.464
98 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 384
99 | 8 | S-Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
100 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
101 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
102 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
103 | 400 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 33200
104 | 12 | Sup Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
105 | 1 | Sup Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
106 | 2 | Sup TrollyMounted Co2 Cylinders(IS-2878) | Elect | Supply | SMR40087 | 9240 | EA | 18480
107 | 2 | Sup Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elect | Supply | SMR40088 | 1386 | SET | 2772
108 | 6 | Sup Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 27720
109 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
110 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
111 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
112 | 1 | Sup Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
113 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
114 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
115 | 1 | Sup Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
116 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
117 | 1 | SupName board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10238 | EA | 10238
118 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
119 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & keycontaining (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23,24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets,6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) AdjustableSpanner 305 mm length least maximum opening 35mmchrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter,(10) Insulated Cutting Plier Length 8” with cable stripperinsulated with thick C. A. sleeve confirming to IS: 4378 - 1990,(11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm,(13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 4925 | SET | 4925
120 | 1 | Sup Rechargeable LED torch light of Standard make | Elect | Supply | SMR40064 | 1733 | EA | 1733
121 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
122 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
123 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
124 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
125 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
126 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | labour | SWR20032 | 1654 | EA | 1654
127 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | labour | SWR22090 | 2205 | EA | 2205
128 | 1 | S-10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
129 | 8.2 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 6273
130 | 28 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 28672
131 | 14 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 46195.8
132 | 28 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 28672
133 | 5500 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11918 | 572.1 | M | 3146550
134 | 1000 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11927 | 1175.56 | M | 1175560
135 | 200 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (excluding the cost of Hume Pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11936 | 1319.84 | M | 263968
136 | 1500 | Laying of 33KV XLPE UG cable Single Run of Size in Hard Rock (1.2*0.45x1=0.54cum) | Elect | Labour | SWR11003 | 1287 | M | 1930500
137 | 82 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 225090
138 | 40 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 228031.2
139 | 1000 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 1044000
140 | 500 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 506000
141 | 200 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 25000
142 | 8 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 22118.08
143 | 70 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 9496.2
144 | 8000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 240000
145 | 82 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 39688
146 | 1.345 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 297.245
147 | 1.345 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 248.825
148 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
149 | 5.845 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2408.6076
150 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
151 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
152 | 18 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 20376
153 | 12 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 11888.16
154 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
155 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
156 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
157 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 74224.278
158 | 0.37 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 1440.41
159 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3340.35
160 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
161 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
162 | 3 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
163 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
164 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
165 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
166 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
167 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | EA | 2640
168 | 6 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
169 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
170 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
171 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
172 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
173 | 6.4 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 4896
174 | 22 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 22528
175 | 11 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 36296.7
176 | 22 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 22528
177 | 3800 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11919 | 465.46 | M | 1768748
178 | 2000 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 2147880
179 | 200 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (cxcluding the cost of Hume Pipe)-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11937 | 1199.4 | M | 239880
180 | 400 | Laying of 11KV XLPE UG cable Single Run in Hard Rock (1.05*0.45x1=0.4725cum) | Elect | Labour | SWR11005 | 1075 | M | 430000
181 | 64 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 175680
182 | 30 | Making of 11 KV 3x300 Sqmm Cable Straight through joints | Elect | Labour | SWR10386 | 3725.45 | EA | 111763.5
183 | 1000 | Supply 4" BClass GI pipe 3.65mm thck 12.2Kg/M | Elect | Supply | SMR40080 | 740 | M | 740000
184 | 300 | Supply 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 227700
185 | 200 | Supply of 4" Hume Pipe | Elect | Supply | SMR40003 | 80 | M | 16000
186 | 16 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
187 | 120 | Raising of Single run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11955 | 144.08 | M | 17289.6
188 | 4500 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 135000
189 | 64 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 30976
190 | 0.614 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 135.694
191 | 0.614 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 113.59
192 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
193 | 4.614 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1901.3371
194 | 16 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
195 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
196 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
197 | 8 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
198 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
199 | 160 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6560
200 | 7.521 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 49480.659
201 | 0.25 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 973.25
202 | 0.23 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Elect | Supply | SWR10869 | 3426 | EA | 787.98
203 | 16 | Supply of CI eath pipe with 80mm dia,2.75mLength | Elect | Supply | SMR11483 | 2789 | EA | 44624
204 | 16 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 19747.2
205 | 16 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 6176
206 | 8 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 640
207 | 8 | Un loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 640
208 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
209 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
210 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
211 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
212 | 40 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 4700
Electrical Total: | [7 empty] | 17632819.6011
Civil Portion:
213 | 24 | Clearing of site by hiring JCB, complete for the finished item of work. | Civil | Labour | SWR34179 | 2165 | Hrs | 51960
214 | 2 | Providing contour surveying maps with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5665 | EA | 11330
215 | 2 | Providing report on soil bearing capacity | Civil | Labour | SWR34097 | 4500 | EA | 9000
216 | 7500 | Design and submisiion of 2 sets of structural design drawings with soft copy complete finished item of work | Civil | Labour | SWR33426 | 5 | FT2 | 37500
217 | 13.82 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work including seigniorage excluding dewatering charges etc as per SS - 20 B(APSS 308).Hard rock ( blasting prohibited ). | Civil | Labour | SWR33018 | 1440 | Cum | 19900.8
218 | 647.44 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work excluding dewatering charges etc as per SS - 20B (APSS 308). Ordinary Soil | Civil | Labour | SWR33015 | 486 | Cum | 314655.84
219 | 72 | Drilling holes in hard granite or sheet rock by Pneumatic compressor 25 mm dia meter etc for complete for item of work | Civil | Labour | SWR34180 | 144 | rmt | 10368
220 | 72 | Grouting the holes with neat cement slurry excluding cost of steel 25 mm dia meter including cost of material labour charges complete fro finished item of work as directed by the engineer in charge | Civil | Labour | SWR34458 | 93 | rmt | 6696
221 | 211.23 | Filling with already available Earthwork in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Civil | Labour | SWR33055 | 202 | Cum | 42668.46
222 | 55.83 | Plain Cement contrete (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4843 | Cum | 270384.69
223 | 67.81 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work. a) Column Footings | Civil | Labour | SWR33098 | 9595 | Cum | 650636.95
224 | 23.87 | RCC M - 20 GF (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. b) Columns" | Civil | Labour | SWR33100 | 13343 | Cum | 318497.41
225 | 15.01 | RCC M - 20 FF (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. b) Columns" | Civil | Labour | SWR33101 | 13343 | Cum | 200278.43
226 | 5.22 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work c)Plinth Beams | Civil | Labour | SWR33099 | 12465 | Cum | 65067.3
227 | 13.46 | RCC M - 20 GF Beams (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all mater as directed by Engineer incharge of the work. d)Roof Beams" | Civil | Labour | SWR33121 | 12381 | Cum | 166648.26
228 | 13.46 | RCC M - 20 FF beams(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all mater as directed by Engineer incharge of the work. d)Roof Beams" | Civil | Labour | SWR33122 | 12381 | Cum | 166648.26
229 | 1.82 | RCC M - 20 GF Lintels(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Lintels | Civil | Labour | SWR33107 | 13173 | Cum | 23974.86
230 | 2.34 | RCC M - 20 FF Lintels(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Lintels | Civil | Labour | SWR33108 | 13173 | Cum | 30824.82
231 | 43.83 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. / h) Roofslab & Staircase "150mm | Civil | Labour | SWR33128 | 10969 | Cum | 480771.27
232 | 32.09 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. / h) Roofslab & Staircase "150mm | Civil | Labour | SWR33129 | 10969 | Cum | 351995.21
233 | 17 | Supplying, fitting and placing HYSD bar reinforcement in foundation complete as per drawings and technical specifications for Bars below 36 mm dia including over laps and wastage, where they are not welded,complete as directed by Engineer incharge of the work. | Civil | Labour | SWR33144 | 75636 | Ton | 1285812
234 | 117.62 | Coursed rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33041 | 5027 | Cum | 591275.74
235 | 50.04 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | Sqm | 6204.96
236 | 65.97 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 8369 | Cum | 552102.93
237 | 47.92 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33069 | 8369 | Cum | 401042.48
238 | 318.9 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification as directed by Engineer incharge of the work. | Civil | Labour | SWR33052 | 493 | Cum | 157217.7
239 | 1190.87 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 559 | Sqm | 665696.33
240 | 932.84 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33164 | 559 | Sqm | 521457.56
241 | 212.86 | 2nd floor Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33165 | 565 | Sqm | 120265.9
242 | 192 | Providng impervious coat to exposed RCC roof slab surface with CM(1:3), 20 mm thick with 1kg of water proof compound per bag of cement laid over roof when it is green including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33156 | 582 | Sqm | 111744
243 | 72.39 | RCM facia 5cm thick in CM (1:3) for drop walls, fins with rabbit wire mesh & nominal reinforcemet as directed by Engineer-in-change with dubara sponge finishing, including cost & conveyance of all materials to site, seigniorage charges, sales & incidental, cost and conveyance of cement, wire mesh, water to work site, centering, scaffolding and form work, lift changes etc., complete for finished items of work but excluding cost of steel & its fabrication charges, for finished item of work. (APSS No.403 & 903). | Civil | Labour | SWR33203 | 3036 | Sqm | 219776.04
244 | 50.4 | Supply & fixing Aluminimum Anodised Two/Three Track Sliding Windows as per approved drawing with aluminium anodised sections of Series C Jindal sections and outer frame top horizontals & both verticals of 8774 of size 62 x 29.5 mm and bottom horizontal - two track frame of 8773 of size 62 x 29.5 mm, Shutter frame top, bottom and verticals of 8304 of size 50 mm x 20 mm and Weather interlocking frame of 8306 of size 50 x 20 with plain clear float glass 5mm thick fixed including Supply & fixing aluminium handles of 100 mm for each shutter, nylon rollers assembly and all labour charges for fixing the fixtures with required no. of screws, bolts and nuts and includingt labour charges for fixing the frame in position, fixing shutter to frame etc. completed for finished item of work | Civil | Labour | SWR33277 | 3623 | Sqm | 182599.2
245 | 62.4 | Supply & fixing of ms grill to windows with outer frame of ISA2525 of 25mm thick , horizontal and vertical square rods of 10x10mm and paintng with synthetic enamel paint per (0.3 x 1.2 )sqm. | Civil | Labour | SWR33310 | 2990 | sqm | 186576
246 | 8.7 | Supplying & fixing collapsible steel shutters with vertical, double channel of 20 x10x2 mm of 100 mm centre ,Bracers with flat iron 40x40x6 mm with 38 mm dia steel pulleys, the top, bottom and side vertical frames of the collapsible gate with 65x65mmx8mm MS Angle and middle guide rail at site height with 65mmx8mm MS flat for the pulleys to guide and fixed with necessary hold fasts, bolts, nuts, rivets, locking arrangements, stoppers, handles, all accessories all fixtures and painted with one coat of approved steel primer etc., complete for finished item of work as per special spn 1105. | Civil | Labour | SWR33411 | 4017 | Sqm | 34947.9
247 | 14.68 | Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood (Schedule Item No. 301.) complete for finished item of work. | Civil | Labour | SWR33269 | 4371 | Sqm | 64166.28
248 | 9.59 | Flooring with cermic tiles of set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33224 | 913 | Sqm | 8755.67
249 | 499 | Flooring with polished shahabad stones 20 mmthick set over base coat of CM (1:3) over already laid CC bed /RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth including cost of all materials like cement, sand, and water and flooring stones etc., complete, including seigniorage charges, labour charges for dresing of flooring stones etc., complete for finished item of work . | Civil | Labour | SWR33219 | 785 | Sqm | 391715
250 | 37.5 | Decorated white back ground glazed tiles, set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste mixed with pigment of matching shadeto full depth, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33226 | 882 | Sqm | 33075
251 | 21.58 | Providing skirting to internal walls to 15 cm height/risers of steps with ...mm thick polished Shahabad stone length equal to polished stones, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete, including seigniorage charges, etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33236 | 723 | Sqm | 15602.34
252 | 582.18 | Painting to new walls with 2 coats of ready mixed oil bound wahsable distemper of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 911 for internal walls as directed by Engineer incharge of the work | Civil | Labour | SWR33333 | 146 | Sqm | 84998.28
253 | 1343.44 | Painting to new walls with 2 coats of ACE paint external grade of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 912 for external walls as directed by Engineer incharge of the work. | Civil | Labour | SWR33334 | 154 | Sqm | 206889.76
254 | 19.18 | Supplying and fixing Alluminium glazed door cum fixed window or door using anodised alluminium extruded sections and mat finish for frames sites and Handle/knib,locking arrangements and 4.0mm plain glass fixed to the frame with beeding and qasket with all required item of work. | Civil | Labour | SWR33272 | 6162 | Sqm | 118187.16
255 | 13.9 | Plain Cement contrete (1:2:4) Nominal Mix using 20 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33030 | 6212 | Cum | 86346.8
256 | 34.64 | Plain Cement contrete (1:3:6) Nominal Mix using 40 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33029 | 5133 | Cum | 177807.12
257 | 2442.25 | Supply and fabrication of beams,chanales and angles including labour charges complete for the finished item of work. | Civil | Labour | SWR33145 | 128 | Kg | 312608
258 | 470.5 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | Rmt | 50814
259 | 2 | Supply & fixing 4 way TPN Distribution board with IP-42 protection suitable for 3 phase 40A FP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 12Nos as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 22706
260 | 6 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 996
261 | 4 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 1796
262 | 56 | Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 37856
263 | 24 | Supply & Fixing of 28W T5 fluorescent tube. Makes : Crompton / Bajaj / Phillips / Surya / Havells with copper choke,starter etc.,incuding 1No 40W tube etc., complete. | Civil | Labour | SWR33558 | 148 | EA | 3552
264 | 1 | Supply of 12" (300mm)ISI, 900 RPM Light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
265 | 270 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | RMT | 20250
266 | 340 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | RMT | 35020
267 | 16 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 2256
268 | 8 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 18216
269 | 8 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 4712
270 | 8 | Supply & Fixing of 12" heavy duty exhaust fan with metal blades etc including all operational, incidental and labour charges etc. complete for the finished item of worK Makes : Crompton / Havells Ventilair-DB / Orient hill air. | Civil | Labour | SWR33573 | 3887 | EA | 31096
271 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
272 | 10 | S&F 20W LED Tubelight Batten | Civil | Labour | SWR33553 | 582 | EA | 5820
273 | 50 | Supplying, laying, jointing and testing 101.4 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | RMT | 37750
274 | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | Civil | Labour | SWR34296 | 8766 | EA | 8766
275 | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 256
276 | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 200
277 | 10 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | RMT | 4620
278 | 5 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | RMT | 2050
279 | 2 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 1534
280 | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap | Civil | Labour | SWR34314 | 2228 | EA | 2228
281 | 1 | Supplying and Fixing best Indian make plastic seat and lid for European water closets with rubber or plastic Buffers as per IS 2548-1996 | Civil | Labour | SWR34315 | 1324 | EA | 1324
282 | 2 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 1442
283 | 4 | S&F 15 mm bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 298 | EA | 1192
284 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
285 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
286 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
287 | 1 | Supplying & Fixing low down Plastic flushing tank 10 Lit Capacity Hindustan Sanitary ware/ parry/ Neycer with internal components | Civil | Labour | SWR34376 | 2032 | EA | 2032
288 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
289 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality complete for finished item of work | Civil | Labour | SWR34426 | 33 | EA | 66
290 | 25 | S & F of (15.90mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | RMT | 5975
291 | 50 | Supply and Fixing of (22.20mm) Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | RMT | 15650
292 | 40 | Supply and Fixing of (28.60mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | RMT | 16400
293 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
294 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 331
295 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
296 | 1 | Supply & fixing NP soap dish heavy type with NP screws | Civil | Labour | SWR34429 | 675 | EA | 675
297 | 17.5 | Supply and fixing of AC sheets including cost of material labour conveyence etc complete for finished item of work as directed by the engineer in charge. | Civil | Labour | SWR33400 | 395 | M2 | 6912.5
298 | 3.05 | S&F of Glow sign board size 10' x 3' including lettering, labour charges, fitting charges cost of all materials and complete for finished item. | Civil | Labour | SWR33422 | 3553 | Sqm | 10836.65
299 | 167.56 | Carting away of excavated soils Complete for finished item of work | Civil | Labour | SWR34151 | 270 | Cum | 45241.2
300 | 7.45 | Providing 20 mm chips in the transformer area including cost, lead and labour charges complete for finished item of work | Civil | Labour | SWR33057 | 1525 | Cum | 11361.25
301 | 20.88 | Supply and fixing of MS GATE with redoxide and 2 Coats of Anamil paint Complete finished item of work as directed by Engineer - in-charge | Civil | Labour | SWR33404 | 5299 | sqm | 110643.12
302 | 1 | Geophysical Investgation charges for water point by Geologist as directed by Engineer in chargecomplete for the finished item of work. | Civil | Labour | SWR33608 | 5000 | Sqm | 5000
303 | 155 | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete 0 to 90M | Civil | Labour | SWR33609 | 336 | Rmt | 52080
304 | 25 | Supply and fixing of 175mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | Rmt | 22075
305 | 1 | Supply and erecting, ISI mark submersible 2.0HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33626 | 21619 | EA | 21619
306 | 120 | Supply and fixing of HDPE pipe 40mm dia of 6Kg/cSqm including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | Rmt | 21600
307 | 1 | Supply and erecting D.O.L Starter 250V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33644 | 1040 | EA | 1040
308 | 180 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | Rmt | 34560
309 | 1 | Provd-DGPS & Total Staion Survey | Civil | Labour | SWR34506 | 5000 | EA | 5000
310 | 1 | Providing supply of electricity to the site premises through custamer service centre duly applying for new connection including service wire, application complete the work. | Civil | Labour | SWR33425 | 5408 | EA | 5408
311 | 366.3 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | Cum | 14652
312 | 700 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | Cum | 68250
313 | 300 | Seigniorage Charges -Gravel | Civil | Labour | SWR34472 | 30 | Cum | 9000
Civil Total | [7 empty] | 10570631.43 | 10570631.43 | 0
Total (Electrical + Civil) | [7 empty] | 28203451.0311 | 17632819.62
18% GST | [7 empty] | 5076621.1856 | 28203451.05
Grand Total ( Elect+ Civil) incl GST | [7 empty] | 33280072.2167 | 0.01888
33280072.239
0.022278

## Sri VenkateshwaraEnclave Park
SCHEDULE
Name of the Work :- Erection of 33/11KV Indoor SS with 2Nos 8MVA PTRs along with Construction of control room, compound wall along with MS gate and borewell, cable trenches, power transformer plinths, toilet block, electrification, sanitary and water supply arrangements for the proposed 33/11 KV Indoor Sub-station at Venkateshwara Nagar colony park, Sirimalle nagar, Rajendranagr in in Rajendra Nagar Constituency of Operation Hyderabad South Circle in Master Plan Circle, Hyderabad.
WBS Element :- S-1772-12-02-02-03-001 WBS No:S-1772-12-07-01-02-001(Civil)
Electrical Portion
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | Code | Rate (INR) | UOM | Amount
1 | 2 | LOADING of 8 MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) - 8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
3 | 2 | UNLOADING of 8 MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
4 | 2 | Erection of 8 MVA PTR | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
5 | 1 | LOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10195 | 350 | EA | 350
6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
7 | 1 | UNLOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10513 | 280 | EA | 280
8 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
9 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc - 3 Phase DTRs 63,75 & 100 KVA | Elect | Labour | SWR20905 | 1650 | EA | 1650
10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space)(excluding of loading unloading) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) (excludingof loading unloading)Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging .Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification | Elect | Supply | SMR40045 | 42000 | EA | 42000
23 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
24 | 8 | LOADING of RSJoists150 x 150 mm/RailPole | Elect | Labour | SWR10205 | 176 | EA | 1408
25 | 8 | UNLOADING of RSJoists150 x150 mm/RailPol | Elect | Labour | SWR10523 | 107 | EA | 856
26 | 0.83 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 183.43
27 | 0.83 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 153.55
28 | 3.83 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1578.2664
29 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
30 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
31 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
32 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
33 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
34 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
35 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 1846.06
36 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
37 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
38 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
39 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
40 | 3.4 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 751.4
41 | 3.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 629
42 | 3.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1401.072
43 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
44 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
45 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
46 | 314 | Paint-Black to all Earth Flat incl. Paint cost | Elect | Labour | SWR12217 | 55 | M | 17270
47 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
48 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
49 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench withearth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
50 | 56 | Raise-33KV 33KV 630sqmm UG Cb on support | Elect | Labour | SWR12448 | 133 | M | 7448
51 | 106 | Lay-33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
52 | 14 | Raising of 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
53 | 8 | S-33KV 1x630Sqmm GIS ID Unit EndTermtn | Elect | Supply | SMR12473 | 2500 | EA | 20000
54 | 8 | S-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Supply | SMR12474 | 4200 | EA | 33600
55 | 8 | Install-33KV 1x630Sqmm GIS ID EndTermtn | Elect | Labour | SWR12473 | 17600 | EA | 140800
56 | 8 | Install-33KV 1x630Sqmm OD Unit EndTermtn | Elect | Labour | SWR12474 | 4000 | EA | 32000
57 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
58 | 85 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
59 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x185 Sqmm Cable | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
60 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
61 | 90 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
62 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
63 | 2 | Supply of 31/2x185Sqmm UG O/D end term kits | Elect | Supply | SMR40140 | 550 | EA | 1100
64 | 2 | Making of Outdoor/Indoor LT 3 1/2 x 185 Sqmm CableCable End Termination | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
65 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 59400
66 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per pecification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
67 | 6 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 456
68 | 1.6 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 659.328
69 | 6 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 300
70 | 1.6 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
71 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
72 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
73 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
74 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
75 | 5 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
76 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
77 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
78 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 603.415
79 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 240
80 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
81 | 1 | Un loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
82 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
83 | 1 | Loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12406 | 80 | EA | 80
84 | 1 | Un loading of 11 KV AB SWCH T.T.200/400 A | Elect | Labour | SWR12425 | 80 | EA | 80
85 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
86 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
87 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
88 | 18 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
89 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elect | Labour | SWR12125 | 14.03 | M | 420.9
90 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
91 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
92 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
93 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 111304
94 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
95 | 8 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
96 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
97 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 965.464
98 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 384
99 | 8 | S-Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
100 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
101 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
102 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
103 | 400 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 33200
104 | 12 | Sup Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
105 | 1 | Sup Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
106 | 2 | Sup TrollyMounted Co2 Cylinders(IS-2878) | Elect | Supply | SMR40087 | 9240 | EA | 18480
107 | 2 | Sup Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elect | Supply | SMR40088 | 1386 | SET | 2772
108 | 6 | Sup Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 27720
109 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
110 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
111 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
112 | 1 | Sup Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
113 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
114 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
115 | 1 | Sup Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
116 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
117 | 1 | SupName board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10238 | EA | 10238
118 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
119 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & keycontaining (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23,24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets,6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) AdjustableSpanner 305 mm length least maximum opening 35mmchrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter,(10) Insulated Cutting Plier Length 8” with cable stripperinsulated with thick C. A. sleeve confirming to IS: 4378 - 1990,(11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm,(13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 4925 | SET | 4925
120 | 1 | Sup Rechargeable LED torch light of Standard make | Elect | Supply | SMR40064 | 1733 | EA | 1733
121 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
122 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
123 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
124 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
125 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
126 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | labour | SWR20032 | 1654 | EA | 1654
127 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | labour | SWR22090 | 2205 | EA | 2205
128 | 1 | S-10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
129 | 8.8 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 6732
130 | 30 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 30720
131 | 15 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 49495.5
132 | 30 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 30720
133 | 5500 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11918 | 572.1 | M | 3146550
134 | 1600 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11927 | 1175.56 | M | 1880896
135 | 200 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (excluding the cost of Hume Pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11936 | 1319.84 | M | 263968
136 | 1500 | Laying of 33KV XLPE UG cable Single Run of Size in Hard Rock (1.2*0.45x1=0.54cum) | Elect | Labour | SWR11003 | 1287 | M | 1930500
137 | 80 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 219600
138 | 30 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 171023.4
139 | 1000 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 1044000
140 | 500 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 506000
141 | 200 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 25000
142 | 8 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 22118.08
143 | 70 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 9496.2
144 | 8800 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 264000
145 | 80 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 38720
146 | 1.345 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 297.245
147 | 1.345 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 248.825
148 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
149 | 5.845 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2408.6076
150 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
151 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
152 | 12 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 13584
153 | 12 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 11888.16
154 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
155 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
156 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
157 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 74224.278
158 | 0.37 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 1440.41
159 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3340.35
160 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
161 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
162 | 3 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
163 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
164 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
165 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
166 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
167 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | EA | 2640
168 | 6 | Supply of CI eath pipe with 80mm dia,2.75m Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
169 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
170 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
171 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
172 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
173 | 6.4 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 4896
174 | 22 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 22528
175 | 11 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 36296.7
176 | 22 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 22528
177 | 3800 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11919 | 465.46 | M | 1768748
178 | 2000 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 2147880
179 | 200 | Excavation & laying of UG Cable in Single Run - laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (cxcluding the cost of Hume Pipe)-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11937 | 1199.4 | M | 239880
180 | 400 | Laying of 11KV XLPE UG cable Single Run in Hard Rock (1.05*0.45x1=0.4725cum) | Elect | Labour | SWR11005 | 1075 | M | 430000
181 | 64 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 175680
182 | 30 | Making of 11 KV 3x300 Sqmm Cable Straight through joints | Elect | Labour | SWR10386 | 3725.45 | EA | 111763.5
183 | 500 | Supply 4" BClass GI pipe 3.65mm thck 12.2Kg/M | Elect | Supply | SMR40080 | 740 | M | 370000
184 | 300 | Supply 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 227700
185 | 200 | Supply of 4" Hume Pipe | Elect | Supply | SMR40003 | 80 | M | 16000
186 | 16 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
187 | 120 | Raising of Single run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11955 | 144.08 | M | 17289.6
188 | 4500 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 135000
189 | 64 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 30976
190 | 0.614 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 135.694
191 | 0.614 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 113.59
192 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
193 | 4.614 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 1901.3371
194 | 16 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
195 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
196 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
197 | 8 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
198 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
199 | 160 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6560
200 | 7.521 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 49480.659
201 | 0.25 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 973.25
202 | 0.23 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Elect | Labour | SWR10869 | 3426 | EA | 787.98
203 | 16 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Supply | SMR11483 | 2789 | EA | 44624
204 | 16 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 19747.2
205 | 16 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 6176
206 | 8 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 640
207 | 8 | Un loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 640
208 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
209 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
210 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
211 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
212 | 40 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 4700
Electrical Total: | [7 empty] | 17929752.5011 | 17929752.45
Civil Portion | [8 empty] | 0.05112
213 | 24 | Clearing of site by hiring JCB, complete for the finished item of work. | Civil | Labour | SWR34179 | 2165 | Hrs | 51960
214 | 2 | Providing contour surveying maps with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5665 | EA | 11330
215 | 2 | Providing report on soil bearing capacity | Civil | Labour | SWR34097 | 4500 | EA | 9000
216 | 7500 | Design and submisiion of 2 sets of structural design drawings with soft copy complete finished item of work | Civil | Labour | SWR33426 | 5 | FT2 | 37500
217 | 27.65 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work including seigniorage excluding dewatering charges etc as per SS - 20 B(APSS 308).Hard rock ( blasting prohibited ). | Civil | Labour | SWR33018 | 1440 | Cum | 39816
218 | 938.7 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work excluding dewatering charges etc as per SS - 20B (APSS 308). Ordinary Soil | Civil | Labour | SWR33015 | 486 | Cum | 456208.2
219 | 108 | Drilling holes in hard granite or sheet rock by Pneumatic compressor 25 mm dia meter etc for complete for item of work | Civil | Labour | SWR34180 | 144 | rmt | 15552
220 | 108 | Grouting the holes with neat cement slurry excluding cost of steel 25 mm dia meter including cost of material labour charges complete fro finished item of work as directed by the engineer in charge | Civil | Labour | SWR34458 | 93 | rmt | 10044
221 | 211.23 | Filling with already available Earthwork in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Civil | Labour | SWR33055 | 202 | Cum | 42668.46
222 | 90.38 | Plain Cement contrete (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4843 | Cum | 437710.34
223 | 82.02 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work. a) Column Footings | Civil | Labour | SWR33098 | 9595 | Cum | 786981.9
224 | 28.46 | RCC M - 20 GF (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. b) Columns" | Civil | Labour | SWR33100 | 13343 | Cum | 379741.78
225 | 4.96 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work c)Plinth Beams | Civil | Labour | SWR33099 | 12465 | Cum | 61826.4
226 | 18.3 | RCC M - 20 GF Beams (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all mater as directed by Engineer incharge of the work. d)Roof Beams" | Civil | Labour | SWR33121 | 12381 | Cum | 226572.3
227 | 1.82 | RCC M - 20 GF Lintels(1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Lintels | Civil | Labour | SWR33107 | 13173 | Cum | 23974.86
228 | 43.83 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. / h) Roofslab & Staircase "150mm | Civil | Labour | SWR33128 | 10969 | Cum | 480771.27
229 | 18 | Supplying, fitting and placing HYSD bar reinforcement in foundation complete as per drawings and technical specifications for Bars below 36 mm dia including over laps and wastage, where they are not welded,complete as directed by Engineer incharge of the work. | Civil | Labour | SWR33144 | 75636 | Ton | 1361448
230 | 240.83 | Coursed rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33041 | 5027 | Cum | 1210652.41
231 | 87.84 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | Sqm | 10892.16
232 | 96.26 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 8369 | Cum | 805599.94
233 | 345.87 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification as directed by Engineer incharge of the work. | Civil | Labour | SWR33052 | 493 | Cum | 170513.91
234 | 1628.63 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 559 | Sqm | 910404.17
235 | 265.28 | Providng impervious coat to exposed RCC roof slab surface with CM(1:3), 20 mm thick with 1kg of water proof compound per bag of cement laid over roof when it is green including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33156 | 582 | Sqm | 154392.96
236 | 90 | RCM facia 5cm thick in CM (1:3) for drop walls, fins with rabbit wire mesh & nominal reinforcemet as directed by Engineer-in-change with dubara sponge finishing, including cost & conveyance of all materials to site, seigniorage charges, sales & incidental, cost and conveyance of cement, wire mesh, water to work site, centering, scaffolding and form work, lift changes etc., complete for finished items of work but excluding cost of steel & its fabrication charges, for finished item of work. (APSS No.403 & 903). | Civil | Labour | SWR33203 | 3036 | Sqm | 273240
237 | 22.33 | Supply & fixing Aluminimum Anodised Two/Three Track Sliding Windows as per approved drawing with aluminium anodised sections of Series C Jindal sections and outer frame top horizontals & both verticals of 8774 of size 62 x 29.5 mm and bottom horizontal - two track frame of 8773 of size 62 x 29.5 mm, Shutter frame top, bottom and verticals of 8304 of size 50 mm x 20 mm and Weather interlocking frame of 8306 of size 50 x 20 with plain clear float glass 5mm thick fixed including Supply & fixing aluminium handles of 100 mm for each shutter, nylon rollers assembly and all labour charges for fixing the fixtures with required no. of screws, bolts and nuts and includingt labour charges for fixing the frame in position, fixing shutter to frame etc. completed for finished item of work | Civil | Labour | SWR33277 | 3623 | Sqm | 80901.59
238 | 26.68 | Supply & fixing of ms grill to windows with outer frame of ISA2525 of 25mm thick , horizontal and vertical square rods of 10x10mm and paintng with synthetic enamel paint per (0.3 x 1.2 )sqm. | Civil | Labour | SWR33310 | 2990 | sqm | 79773.2
239 | 7.95 | Supplying & fixing collapsible steel shutters with vertical, double channel of 20 x10x2 mm of 100 mm centre ,Bracers with flat iron 40x40x6 mm with 38 mm dia steel pulleys, the top, bottom and side vertical frames of the collapsible gate with 65x65mmx8mm MS Angle and middle guide rail at site height with 65mmx8mm MS flat for the pulleys to guide and fixed with necessary hold fasts, bolts, nuts, rivets, locking arrangements, stoppers, handles, all accessories all fixtures and painted with one coat of approved steel primer etc., complete for finished item of work as per special spn 1105. | Civil | Labour | SWR33411 | 4017 | Sqm | 31935.15
240 | 3.7 | Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood (Schedule Item No. 301.) complete for finished item of work. | Civil | Labour | SWR33269 | 4371 | Sqm | 16172.7
241 | 9.59 | Flooring with cermic tiles of set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33224 | 913 | Sqm | 8755.67
242 | 225.78 | Flooring with polished shahabad stones 20 mmthick set over base coat of CM (1:3) over already laid CC bed /RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth including cost of all materials like cement, sand, and water and flooring stones etc., complete, including seigniorage charges, labour charges for dresing of flooring stones etc., complete for finished item of work . | Civil | Labour | SWR33219 | 785 | Sqm | 177237.3
243 | 12.5 | Decorated white back ground glazed tiles, set over base coat of cement mortar (1:3) 20 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste mixed with pigment of matching shadeto full depth, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33226 | 882 | Sqm | 11025
244 | 18.22 | Providing skirting to internal walls to 15 cm height/risers of steps with ...mm thick polished Shahabad stone length equal to polished stones, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete, including seigniorage charges, etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33236 | 875 | Sqm | 15942.5
245 | 576.18 | Painting to new walls with 2 coats of ready mixed oil bound wahsable distemper of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 911 for internal walls as directed by Engineer incharge of the work | Civil | Labour | SWR33333 | 146 | Sqm | 84122.28
246 | 1526.94 | Painting to new walls with 2 coats of ACE paint external grade of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 912 for external walls as directed by Engineer incharge of the work. | Civil | Labour | SWR33334 | 154 | Sqm | 235148.76
247 | 9.59 | Supplying and fixing Alluminium glazed door cum fixed window or door using anodised alluminium extruded sections and mat finish for frames sites and Handle/knib,locking arrangements and 4.0mm plain glass fixed to the frame with beeding and qasket with all required item of work. | Civil | Labour | SWR33272 | 6162 | Sqm | 59093.58
248 | 19.68 | Plain Cement contrete (1:2:4) Nominal Mix using 20 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33030 | 6212 | Cum | 122252.16
249 | 30.14 | Plain Cement contrete (1:3:6) Nominal Mix using 40 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33029 | 5133 | Cum | 154708.62
250 | 2354.44 | Supply and fabrication of beams,chanales and angles including labour charges complete for the finished item of work. | Civil | Labour | SWR33145 | 128 | Kg | 301368.32
251 | 333 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | Rmt | 35964
252 | 1 | Supply & fixing 4 way TPN Distribution board with IP-42 protection suitable for 3 phase 40A FP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 12Nos as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
253 | 8 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1328
254 | 2 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 898
255 | 64 | Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 43264
256 | 24 | Supply & Fixing of 28W T5 fluorescent tube. Makes : Crompton / Bajaj / Phillips / Surya / Havells with copper choke,starter etc.,incuding 1No 40W tube etc., complete. | Civil | Labour | SWR33558 | 148 | EA | 3552
257 | 1 | Supply of 12" (300mm)ISI, 900 RPM Light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
258 | 186 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | RMT | 13950
259 | 308 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | RMT | 31724
260 | 16 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 2256
261 | 12 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 27324
262 | 12 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 7068
263 | 10 | Supply & Fixing of 12" heavy duty exhaust fan with metal blades etc including all operational, incidental and labour charges etc. complete for the finished item of worK Makes : Crompton / Havells Ventilair-DB / Orient hill air. | Civil | Labour | SWR33573 | 3887 | EA | 38870
264 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
265 | 10 | S&F 20W LED Tubelight Batten | Civil | Labour | SWR33553 | 582 | EA | 5820
266 | 35 | Supplying, laying, jointing and testing 101.4 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | RMT | 26425
267 | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | Civil | Labour | SWR34296 | 8766 | EA | 8766
268 | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 256
269 | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 200
270 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | RMT | 5544
271 | 5 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | RMT | 2050
272 | 2 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 1534
273 | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap | Civil | Labour | SWR34314 | 2228 | EA | 2228
274 | 1 | Supplying and Fixing best Indian make plastic seat and lid for European water closets with rubber or plastic Buffers as per IS 2548-1996 | Civil | Labour | SWR34315 | 1324 | EA | 1324
275 | 2 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 1442
276 | 4 | S&F 15 mm bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 298 | EA | 1192
277 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
278 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
279 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
280 | 1 | Supplying & Fixing low down Plastic flushing tank 10 Lit Capacity Hindustan Sanitary ware/ parry/ Neycer with internal components | Civil | Labour | SWR34376 | 2032 | EA | 2032
281 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
282 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality complete for finished item of work | Civil | Labour | SWR34426 | 33 | EA | 66
283 | 20 | S & F of (15.90mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | RMT | 4780
284 | 50 | Supply and Fixing of (22.20mm) Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | RMT | 15650
285 | 40 | Supply and Fixing of (28.60mm)Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | RMT | 16400
286 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
287 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 331
288 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
289 | 1 | Supply & fixing NP soap dish heavy type with NP screws | Civil | Labour | SWR34429 | 675 | EA | 675
290 | 17.5 | Supply and fixing of AC sheets including cost of material labour conveyence etc complete for finished item of work as directed by the engineer in charge. | Civil | Labour | SWR33400 | 395 | M2 | 6912.5
291 | 3.05 | S&F of Glow sign board size 10' x 3' including lettering, labour charges, fitting charges cost of all materials and complete for finished item. | Civil | Labour | SWR33422 | 3553 | M2 | 10836.65
292 | 195 | Carting away of excavated soils Complete for finished item of work | Civil | Labour | SWR34151 | 270 | Cum | 52650
293 | 6.27 | Providing 20 mm chips in the transformer area including cost, lead and labour charges complete for finished item of work | Civil | Labour | SWR33057 | 1525 | Cum | 9561.75
294 | 30 | Flooring with chequrred terrazzo tiles of 22 mm thick (medium shade ) set over base coat of cement mortar (1:6) 12 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, complete for finished item of work | Civil | Labour | SWR33222 | 916 | Sqm | 27480
295 | 8.75 | Supply and fixing of MS GATE with redoxide and 2 Coats of Anamil paint Complete finished item of work as directed by Engineer - in-charge | Civil | Labour | SWR33404 | 5299 | sqm | 46366.25
296 | 1 | Geophysical Investgation charges for water point by Geologist as directed by Engineer in chargecomplete for the finished item of work. | Civil | Labour | SWR33608 | 5000 | EA | 5000
297 | 185 | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete 0 to 90M | Civil | Labour | SWR33609 | 336 | Rmt | 62160
298 | 25 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | Rmt | 22075
299 | 1 | Supply and erecting, ISI mark submersible 2.0HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33626 | 21619 | EA | 21619
300 | 168 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cSqm including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | Rmt | 30240
301 | 1 | Supply and erecting D.O.L Starter 250V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33644 | 1040 | EA | 1040
302 | 180 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | Rmt | 34560
303 | 1 | Provd-DGPS & Total Staion Survey | Civil | Labour | SWR34506 | 5000 | EA | 5000
304 | 1 | Providing supply of electricity to the site premises through custamer service centre duly applying for new connection including service wire, application complete the work. | Civil | Labour | SWR33425 | 5408 | EA | 5408
305 | 290 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | Cum | 11600
306 | 558.84 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | Cum | 54486.9
307 | 345.88 | Seigniorage Charges -Gravel | Civil | Labour | SWR34472 | 30 | Cum | 10376.4
Civil Total | [7 empty] | 10099971.34
Total(Elect+Civil) | [7 empty] | 28029723.8411
GST @ 18 % | [7 empty] | 5045350.2914
Grand Total (Elect +Civil) incl GST | [7 empty] | 33075074.1325